## Rules
App G Section ID | Rule ID | Rule Description | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Applicable RMR | Note | Complexity | Importance | Triggers
1 | 1 | User RMR has same number of spaces as Baseline RMR | Baseline RMR = User RMR | None | No | Baseline
1 | 2 | User RMR has same number of spaces as Propsoed RMR | Proposed RMR = User RMR | None | No | Proposed
1 | 3 | Baseline shall be modeled with the same conditioned floor area as User RMR | Baseline RMR = User RMR | none | No | Baseline | This is a whole building rule not a space by space rule. Individual Spaces are tested using a different rule.
1 | 4 | Proposed shall be modeled with same conditioned floor area as User RMR | Proposed RMR = User RMR | none | No | Proposed | This is a whole building rule not a space by space rule.
1 | 5 | Baseline shall be modeled with the same number of floors | Baseline RMR = User RMR | none | No | Baseline
1 | 6 | Proposed shall be modeled with same number of floors | Proposed RMR = User RMR | none | No | Proposed
1 | 7 | User RMR spaces have corresponding space in Baseline RMR (using space name) | Baseline RMR = User RMR | None | No | Baseline
1 | 8 | User RMR space has same area as corresponding space in Baseline RMR | Baseline RMR = User RMR | Rule 7 | No | Baseline
1 | 9 | User RMR space has same space_cond_type as corresponding space in Baseline RMR | Baseline RMR = User RMR | Rule 7 | No | Baseline
1 | 10 | User RMR spaces have corresponding space in Propsoed RMR (using space name) | Proposed RMR = User RMR | None | No | Proposed
1 | 11 | User RMR space has same area as corresponding space in Proposed RMR | Proposed RMR = User RMR | Rule 10 | No | Proposed
1 | 12 | User RMR space has same space_cond_type as corresponding space in Proposed RMR | Proposed RMR = User RMR | Rule 10 | No | Proposed
1 | 13 | User RMR space_use_type is approved for heated_only space_cond_type ( storage rooms, stairwells, vestibules, electrical/mechanical rooms, and restrooms not exhausting or transferring air from mechanically cooled thermal zones) | User RMR = expected value |  | Yes | User | Rule 9 and 12 catch cases when Baseline or Proposed don't match user RMR. Using different rules doesn't directly catch that Baseline or Proposed are not allowed to be heated only
1 |  | When the performance rating method is applied to buildings in which energy-related features have not yet been designed (e.g., a lighting system), those yet-to-be-designed features shall be described in the User Model exactly as they are defined in the baseline building design. | User RMR = Baseline RMR |  |  | User | How can we test this?
1 |  | When the performance rating method is applied to buildings in which energy-related features have not yet been designed the proposed design shall be the same as the User Model. | Proposed RMR = User RMR |  |  | Proposed
1 |  | Except as instructed, all building systems and equipment shall be modeled identically in the User design and baseline design. | Proposed RMR = User RMR |  |  | Proposed
1 |  | Except as instructed, all building systems and equipment shall be modeled identically in the User design and baseline design. | Baseline RMR = User RMR |  |  | Baseline
1 |  | Where the space classification for a space is not known, the space shall be categorized as an office space. | User RMR = expected value |  |  | User
1 |  | Where the baseline building systems and equipment are permitted to be different from the proposed design but are not prescribed in this appendix, the baseline must be determined based on the following, in the order of priority: a. Requirements in Sections 5 through 10 b. Requirements of other efficiency or equipment codes or standards applicable to the design of the building systems and equipment. | User RMR = expected value |  |  | User
3 | 1 | Space Use Classification in the Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 1-7 passes | No | Baseline
3 | 2 | Space Use Classification in the Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 1-10 passes | No | Proposed
3 | 3 | Space use Classification in the User RMR is from Table 9.6-1 | User RMR = expected value | none | Yes | User | Does the RMR need to allow multiple space use classifications to be defined for a single thermal block?
3 | 4 | Space Use Classification in the User RMR is from Table 9.5-1 | User RMR = expected value | Rule 3-3 = false | Yes | User

## Schema Data Elements
Data Group | Attribute Names (variables needed for test) | Std 229 Schema Name | Description | Units | Type | Enumerations
Space | ID |  | Spae ID | None | number
Space | Name |  | Space Name | none | Text
Space | floor_area |  | Floor area of a space | m2 | Number | any integer > 0
Space | cond_type |  | Space conditiponing category | none | Type | heated_and_cooled, heated_only, semiheated, unconditioned, plenum
Space | use_class |  | Whether space use types are building area types from Table 9.5.1 or space use types from Table 9.6.1 | none | list | (all area types from table 9.6-1 or 9.5-1
Building | number_of_floors |  | Number of floors in building | none | Number | any integer > 0
Note on D15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Test Case Descriptions
App G Section ID | Rule ID | Test ID | Unique ID | Rule Description | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Test Scope | Test Description | RMR Tested | Expected Test Outcome | Test Outcome Text | RMR Attribute Names (variables needed for test) | User RMR Value(s) | Proposed RMR Value(s) | Baseline RMR Value(s) | Test Case RMR Template | Note
Table G3.1 Prt 1.
1 | 1 | a | 1-1a | Number of spaces modeled in User RMR and Baseline RMR are the same | Baseline RMR = User RMR | none | No | Per project | Space count in Baseline RMR = User RMR | Baseline | Pass | The same number of spaces are reported in both the Baseline and User RMR files | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 |  | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 | One Story Template
1 | 1 | b | 1-1b | Number of spaces modeled in User RMR and Baseline RMR are the same | Baseline RMR = User RMR | none | No | Per project | Space count in Baseline RMR > User RMR | Baseline | Fail | The number of reported spaces in the User RMR is less than the Baseline RMR | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 null (empty) null (empty) |  | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 6 space_6 | One Story Template
1 | 1 | c | 1-1c | Number of spaces modeled in User RMR and Baseline RMR are the same | Baseline RMR = User RMR | none | No | Per project | Space count in Baseline RMR < User RMR | Baseline | Fail | The number of reported spaces in the User RMR is greater than the Baseline RMR | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 6 space_6 |  | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 null (empty) null (empty) | One Story Template
1 | 2 | a | 1-2a | Number of spaces modeled in User RMR and Proposed RMR are the same | Proposed RMR = User RMR | none | No | Per project | Space count in Proposed RMR = User RMR | Proposed | Pass | The same number of spaces are reported in both the Proposed and User RMR files | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 |  | One Story Template
1 | 2 | b | 1-2b | Number of spaces modeled in User RMR and Proposed RMR are the same | Proposed RMR = User RMR | none | No | Per project | Space count in Proposed RMR > User RMR | Proposed | Fail | The number of reported spaces in the User RMR is less than the Proposed RMR | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 null (empty) null (empty) | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 6 space_6 |  | One Story Template
1 | 2 | c | 1-2c | Number of spaces modeled in User RMR and Proposed RMR are the same | Proposed RMR = User RMR | none | No | Per project | Space count in Proposed RMR < User RMR | Proposed | Fail | The number of reported spaces in the User RMR is greater than the Proposed RMR | space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name space: ID space: name | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 6 space_6 | 1 space_1 2 space_2 3 space_3 4 space_4 5 space_5 null (empty) null (empty) |  | One Story Template
1 | 3 | a | 1-3a | User RMR total floor area of each space_cond_type = Baseline total floor area of each space_cond_type | Baseline RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas equal Baseline RMR {space_cond_type} floor areas | Baseline | Pass | The space conditioned floor areas reported in the User RMR are the same as the Baseline RMR. | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled |  | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled | One Story Template
1 | 3 | b | 1-3b | User RMR total floor area of each space_cond_type = Baseline total floor area of each space_cond_type | Baseline RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas not equal to Baseline RMR {space_cond_type} floor areas (different cond types, same total area) | Baseline | Fail | The heated and cooled floor area in the User RMR does not match the Baseline RMR (suggest that for per project report output table of values showing all space cond types) | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled |  | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_only 5 1500 heated_and_cooled | One Story Template
1 | 3 | b | 1-3b | User RMR total floor area of each space_cond_type = Baseline total floor area of each space_cond_type | Baseline RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas not equal to Baseline RMR {space_cond_type} floor areas | Baseline | Fail | The heated and cooled floor area in the User RMR does not match the Baseline RMR | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled |  | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1400 heated_and_cooled | One Story Template
1 | 4 | a | 1-4a | User RMR total floor area of each space_cond_type = Proposed total floor area of each space_cond_type | Proposed RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas equal Proposed RMR {space_cond_type} floor areas | Proposed | Pass | The space conditioned floor areas reported in the User RMR are the same as the Proposed RMR. | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled |  | One Story Template
1 | 4 | b | 1-4b | User RMR total floor area of each space_cond_type = Proposed total floor area of each space_cond_type | Proposed RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas not equal to Proposed RMR {space_cond_type} floor areas (different cond types, same total area) | Proposed | Fail | The heated and cooled floor area in the User RMR does not match the Proposed RMR (suggest that for per project report output table of values showing all space cond types) | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_only 5 1500 heated_and_cooled |  | One Story Template
1 | 4 | c | 1-4c | User RMR total floor area of each space_cond_type = Proposed total floor area of each space_cond_type | Proposed RMR = User RMR | none | No | Per space_cond_type | User RMR {space_cond_type} floor areas not equal to Proposed RMR {space_cond_type} floor areas | Proposed | Fail | The heated and cooled floor area in the User RMR does not match the Proposed RMR | space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type space: ID space: floor_area space: cond_type | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and_cooled 5 1500 heated_and_cooled | 1 500 heated_and_cooled 2 500 heated_and_cooled 3 500 heated_and_cooled 4 500 heated_and _cooled 5 1400 heated_and_cooled |  | One Story Template
1 | 5 | a | 1-5a | Number of Floors reported in User RMR equals number of floors reported in Baseline RMR | Baseline RMR = User RMR | none | no | per project | User RMR number of floors equals Baseline RMR number of Floors | Baseline | Pass | The number of floors reported in the Baseline RMR is the same as the User RMR | Building: number-of_floors | 1 |  | 1 | One Story Template
1 | 5 | b | 1-5b | Number of Floors reported in User RMR equals number of floors reported in Baseline RMR | Baseline RMR = User RMR | none | no | per project | User RMR number of floors does not equal the Baseline RMR number of floors | Baseline | Fail | The number of floors reported in the Baseline RMR does not match the User RMR | Building: number-of_floors | 1 |  | 2 | One Story Template
1 | 6 | a | 1-6a | Number of Floors reported in User RMR equals number of floors reported in Proposed RMR | Proposed RMR = User RMR | none | no | per project | User RMR number of floors equals Proposed RMR number of Floors | Proposed | Pass | The number of floors reported in the Proposed RMR is the same as the User RMR | Building: number-of_floors | 1 | 1 |  | One Story Template
1 | 6 | b | 1-6b | Number of Floors reported in User RMR equals number of floors reported in Proposed RMR | Proposed RMR = User RMR | none | no | per project | User RMR number of floors does not equal the Proposed RMR number of floors | Proposed | Fail | The number of floors reported in the Proposed RMR does not match the User RMR | Building: number-of_floors | 1 | 2 |  | One Story Template
1 | 7 | a | 1-7a | Each space reported in the User RMR has a corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | none | No | Per space | All User RMR spaces (via names) are included in Baseline RMR | Baseline | Pass | {space_name_1} in the User RMR has a corresponding space in the Baseline RMR | space: name | space_1 |  | space_1 | One Story Template
1 | 7 | b | 1-7b | Each space reported in the User RMR has a corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | none | No | Per space | User RMR spaces (via space name) do not match the Baseline RMR | Baseline | Fail | It cannot be confirmed that {space_name_2} in the User RMR has a corresponding space in the Baseline RMR | space: name space: name | space_1 space_2 |  | space_1 space_24 | One Story Template | All tests in Appendix G Sections 2-16 depend on knowing the relationship between the different spaces in the RMR triplet.
1 | 8 | a | 1-8a | Each space reported in the User RMR has the same floor area as the corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | Rule 1-7 = True | No | Per space | Floor areas of User RMR spaces match floor areas of corresponding spaces (via names) in Baseline RMR | Baseline | Pass | Floor area of {space_name_1} in the User RMR matches floor area of the corresponding space in the Baseline RMR | space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 |  | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 | One Story Template | we only care about efficiency matching so the phase being incorrect doesn't matter.
1 | 8 | b | 1-8b | Each space reported in the User RMR has the same floor area as the corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | Rule 1-7 = True | No | Per space | Floor area of User RMR spaces do not match floor areas of corresponding spaces (via names) in Baseline RMR | Baseline | Fail | Floor area of {space:name} space_2 in the User RMR does not match the floor area of the corresponding space in the Baseline RMR | space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 |  | space_1 500 space_2 550 space_3 500 space_4 500 space_5 1500 | One Story Template | May require further interpretation of requirements. Does capacity ratio need to be the same if fluid-filled modeled? Also for Schema does data element require just capacity ratio or capacity and peak load?
1 | 9 | a | 1-9a | Each space reported in the User RMR has the same space conditioning type as the corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | Rule 1-7 = true | No | Per space | Space condition type of User RMR spaces matches the Space condition type of the corresponding spaces (via names) in Baseline RMR | Baseline | Pass | The space condition type of {space:name} in the User RMR matches the space condition type of the corresponding space in the Baseline RMR | space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled |  | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled | One Story Template
1 | 9 | b | 1-9b | Each space reported in the User RMR has the same space conditioning type as the corresponding space in the Baseline RMR. (Confirmed by matching space names) | Baseline RMR = User RMR | Rule 1-7 = true | No | Per space | Floor area of User RMR spaces do not match floor areas of corresponding spaces (via names) in Baseline RMR | Baseline | Pass | The space condition type of {space:name} Space_3 in the User RMR does not match the space condition type of the corresponding space in the Baseline RMR | space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled |  | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_only space_4 heated_and_cooled space_5 heated_and_cooled | One Story Template
1 | 10 | a | 1-10a | Each space reported in the User RMR has a corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | none | No | Per space | All User RMR spaces (via names) are included in Proposed RMR | Proposed | Pass | {space_name_1} in the User RMR has a corresponding space in the Proposed RMR | space: name | space_1 | space_1 |  | One Story Template
1 | 10 | b | 1-10b | Each space reported in the User RMR has a corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | none | No | Per space | User RMR spaces (via space name) do not match the Proposed RMR | Proposed | Fail | It cannot be confirmed that {space_name_2} in the User RMR has a corresponding space in the Proposed RMR | space: name space: name | space_1 space_2 | space_1 space_24 |  | One Story Template | All tests in Appendix G Sections 2-16 depend on knowing the relationship between the different spaces in the RMR triplet.
1 | 11 | a | 1-11a | Each space reported in the User RMR has the same floor area as the corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | Rule 1-10 = True | No | Per space | Floor areas of User RMR spaces match floor areas of corresponding spaces (via names) in Proposed RMR | Proposed | Pass | Floor area of {space_name_1} in the User RMR matches floor area of the corresponding space in the Proposed RMR | space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 |  | One Story Template | we only care about efficiency matching so the phase being incorrect doesn't matter.
1 | 11 | b | 1-11b | Each space reported in the User RMR has the same floor area as the corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | Rule 1-10 = True | No | Per space | Floor area of User RMR spaces do not match floor areas of corresponding spaces (via names) in Proposed RMR | Proposed | Pass | Floor area of {space_name_2} in the User RMR does not match the floor area of the corresponding space in the Proposed RMR | space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area space: name space: floor_area | space_1 500 space_2 500 space_3 500 space_4 500 space_5 1500 | space_1 500 space_2 550 space_3 500 space_4 500 space_5 1500 |  | One Story Template | May require further interpretation of requirements. Does capacity ratio need to be the same if fluid-filled modeled? Also for Schema does data element require just capacity ratio or capacity and peak load?
1 | 12 | a | 1-12a | Each space reported in the User RMR has the same space conditioning type as the corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | Rule 1-10 = true | No | Per space | Space condition type of User RMR spaces matches the Space condition type of the corresponding spaces (via names) in Proposed RMR | Proposed | Pass | The spacce condition type of {space_name_1} in the User RMR matches the space condition type of the corresponding space in the Proposed RMR | space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled |  | One Story Template
1 | 12 | b | 1-12b | Each space reported in the User RMR has the same space conditioning type as the corresponding space in the Proposed RMR. (Confirmed by matching space names) | Proposed RMR = User RMR | Rule 1-10 = true | No | Per space | Floor area of User RMR spaces do not match floor areas of corresponding spaces (via names) in Proposed RMR | Proposed | Pass | Floor area of {space_name_2} in the User RMR does not match the floor area of the corresponding space in the Proposed RMR | space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type space: name space: cond_type | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_and_cooled space_4 heated_and_cooled space_5 heated_and_cooled | space_1 heated_and_cooled space_2 heated_and_cooled space_3 heated_only space_4 heated_and_cooled space_5 heated_and_cooled |  | One Story Template
1 | 13 | a | 1-13a | Each space reported in the User RMR with space_cond_type = heated_only is assigned an approved space_use_type | User RMR = expected value | None | Yes (approved heating only use types) | Per space | Space use type of User RMR spaces with space_cond_type =heated_only are all approved types | User | Pass | {space: name} Space_4 in the User RMR is assigned an approved space use type for a heated only space. | space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class | space_1 heated_and_cooled office_enclosed space_2 heated_and_cooled office_enclosed space_3 heated_and_cooled office_enclosed space_4 heated_only stairwell space_5 heated_and_cooled office_enclosed |  |  | One Story Template
1 | 13 | b | 1-13b | Each space reported in the User RMR with space_cond_type = heated_only is assigned an approved space_use_type | User RMR = expected value | None | Yes (approved heating only use types) | Per space | Space use type of User RMR spaces with space_cond_type =heated_only are not all approved types | User | Fail | {space:name} Space_5 in the User RMR does not have an approved space use type for a heated only space. | space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class | space_1 heated_and_cooled office_enclosed space_2 heated_and_cooled office_enclosed space_3 heated_and_cooled office_enclosed space_4 heated_only stairwell space_5 heated_only office_enclosed |  |  | One Story Template
1 | 13 | c | 1-13c | Each space reported in the User RMR with space_cond_type = heated_only is assigned an approved space_use_type | User RMR = expected value | None | Yes (approved heating only use types) | Per space | Space use type uses value from Table 9.5.1 but does not use warehouse space type | User | Fail | {space:name} Space_4 in the User RMR does not have an approved space use type for a heated only space. | space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class | space_1 heated_and_cooled office_enclosed space_2 heated_and_cooled office_enclosed space_3 heated_and_cooled office_enclosed space_4 heated_only Automotive_Facility space_5 heated_only stairwell |  |  | One Story Template
1 | 13 | d | 1-13d | Each space reported in the User RMR with space_cond_type = heated_only is assigned an approved space_use_type | User RMR = expected value | None | Yes (approved heating only use types) | Per space | Space use type value is not an approved enumeration for space: use_class | User | Fail | {space: name} Space _4 in the User RMR is reported as a heating only space but the space use classification "Stairs" is not an allowable space type so it cannot be confirmed that this is an approved use for a heating_only space type. | space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class space: name space: cond_type space: use_class | space_1 heated_and_cooled office_enclosed space_2 heated_and_cooled office_enclosed space_3 heated_and_cooled office_enclosed space_4 heated_only stairs space_5 heated_and_cooled office_enclosed |  |  | One Story Template
3 | 1 | a | 3-1a | Space Use Classification in the Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 1-7 passes | Yes (use classifications) | Per space | Space use classification of each space in Baseline RMR matches the use classification of the corresponding space in the User RMR | Baseline | Pass | The space use classifications of all spaces in the Baseline RMR match the use classifications of the corresponding spaces in the User RMR | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed |  | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed
3 | 1 | b | 3-1b | Space Use Classification in the Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 1-7 passes | Yes (use classifications) | Per space | Space use classification of each space in Baseline RMR matches the use classification of the corresponding space in the User RMR | Baseline | Fail | The space use classification of {space:name} Space_4 in the Baseline RMR does not match the use classifications of the corresponding space in the User RMR | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed |  | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 office_enclosesd space_5 office_enclosed
3 | 2 | a | 3-2a | Space Use Classification in the Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 1-10 passes | Yes (use classifications) | Per space | Space use classification of each space in Proposed RMR matches the use classification of the corresponding space in the User RMR | Proposed | Pass | The space use classifications of all spaces in the Proposed RMR match the use classifications of the corresponding spaces in the User RMR | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed
3 | 2 | b | 3-2b | Space Use Classification in the Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 1-10 passes | Yes (use classifications) | Per space | Space use classification of each space in Proposed RMR matches the use classification of the corresponding space in the User RMR | Proposed | Fail | The space use classification of {space:name} Space_4 in the Proposed RMR does not match the use classifications of the corresponding space in the User RMR | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 office_enclosesd space_5 office_enclosed
3 | 3 | a | 3-3a | Space Use Classifications in the User RMR are from Table 9.6-1 | User RMR = expected value | none | Yes (use classifications) | Per space | Space use classification of each space in User RMR is from Table 9.6-1 | User | Pass | The space use classification of {space: name} in the User RMR match the use classification in Table 9.6-1 | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 stairwell space_5 office_enclosed
3 | 3 | b | 3-3b | Space Use Classifications in the User RMR are from Table 9.6-1 | User RMR = expected value | none | Yes (use classifications) | Per space | Space use classification of Space_4 in User RMR is not from Table 9.6-1, all others are | User | Fail | The space use classification of {space: name} Space_4 in the User RMR does not match a use classification in Table 9.6-1 | space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class space: name space: use_class | space_1 office_enclosed space_2 office_enclosed space_3 office_enclosed space_4 fire_station space_5 office_enclosed
3 | 4 | a | 3-4a | Space Use Classification in the User RMR is from Table 9.5-1 | User RMR = expected value | Rule 3-3 fails or is false | Yes (use classifications) | Per space | Space use classification of Space_4 in User RMR is from Table 9.5-1 | User | Pass | The space use classifications of Space_4 is from Table 9.5-1, confirm space is eligible to use Table 9.5-1 value | space: name space: use_class | space_4 fire_station
3 | 4 | b | 3-4b | Space Use Classification in the User RMR is from Table 9.5-1 | User RMR = expected value | Rule 3-3 fails or is false | Yes (use classifications) | Per space | Space use classification of Space_4 in User RMR is from Table 9.5-1 | User | Fail | The space use classification of Space_4 is not of an allowable type, confirm correct space type | space: name space: use_class | space_4 Stairs
-
Last Row of Table
Note on S22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)