## ListofRules (hidden)
Unique ID | Rule ID |  | Class 1 | Class 2 | Class 3 | 2016 | 2019 | App G Section | Proposed Building Requirement | Baseline Building Requirement | Triggers
139 | 18 | 139-18 | HVAC Waterside | Heating | Type | Y | Y | G3.1.1.1 & G3.1.1.3.1 | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. Hot-water or steam costs shall be based on actual utility rates, | Purchased heat source and rates shall be the same as the proposed and on-site boilers, electric heat, and furnaces shall not be modeled in the baseline building design.
144 | 18 | 144-18 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.1.3.4 | When a proposed desgin includes purchased heat all on-site distribution pumps shall be modeled in both the proposed design and base building design. | Baseline should include all on-site distribution pumps included int he Proposed design
147 | 19 | 147-19 | HVAC Waterside | Heating | Capacity | Y | Y | G3.1.2.2 | As- Designed | Plant capacities shall be based on coincident loads.
173 | 21 | 173-21 | HVAC Waterside | Heating | Equipment | Y | Y | G3.1.3.2 | As-Designed | When baseline building does not use purchased heat, baseline systems 1,5,7,11, 12 shall be modeled with natural draft boilers
174 | 21 | 174-21 | HVAC Waterside | Heating | Capacity | Y | Y | G3.1.3.2 | As-Designed | When baseline building includes boilers model 2 equal sized boilers when conditioned floor area > 15,000 ft sized equally, otherwise model a single boiler.
175 | 21 | 175-21 | HVAC Waterside | Heating | Controls | Y | Y | G3.1.3.2 | As-Designed | When baseline building includes two boilers each shall stage as required by load.
176 | 21 | 176-21 | HVAC Waterside | Heating | Capacity | Y | Y | G3.1.3.3 | As-Designed | When baseline building requires boilers, systems 1,5,7,11 and 12 - Model HWST = 180F and return design temp = 130F
177 | 21 | 177-21 | HVAC Waterside | Heating | Controls | Y | Y | G3.1.3.4 | As-Designed | For systems 1,5,7,11 and 12 - HWST reset using OA reset schedule 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F.
178 | 21 | 178-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When baseline building includes boilers, Hot Water Pump Power = 19W/gpm
179 | 21 | 179-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When the building uses boilers the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD.
180 | 21 | 180-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When the system uses boilers the hot water system shall be modeled as primary only with continuous variable flow and a minimum turndown of 25%.
182 | 21 | 182-21 | HVAC Waterside | Heating | Equipment | Y | Y | G3.1.3.2 | As-Designed | When baseline building uses purchased heat, No boilers shall be modeled
183 | 21 | 183-21 | HVAC Waterside | Heating | Capacity | Y | Y | G3.1.3.3 | As-Designed | When baseline building uses purchased HW baseline system hot water system shallbe modeled so - Model HWST = 180F and return design temp = 130F
184 | 21 | 184-21 | HVAC Waterside | Heating | Controls | Y | Y | G3.1.3.4 | As-Designed | When baseline building uses purchased heat do not model supply temperature reset.
185 | 21 | 185-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When baseline building uses purchased heat hot water pump power = 14W/gpm
186 | 21 | 186-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When the building uses purchased heat the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD.
187 | 21 | 187-21 | HVAC Waterside | Heating | Pumps | Y | Y | G3.1.3.5 | As-Designed | When the building uses purchased heat the hot water system shall be modeled as primary only with continuous variable flow and a minimum turndown of 25%.

## Rules
Unique ID | Rule ID | Rule ID2 | App G Section | Proposed Building Requirement | Baseline Building Requirement | Rule Description | Applicable RMR | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Note
139 | 18 | 139-18 | G3.1.1.1 & G3.1.1.3.1 | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. Hot-water or steam costs shall be based on actual utility rates, | Purchased heat source and rates shall be the same as the proposed and on-site boilers, electric heat, and furnaces shall not be modeled in the baseline building design. | For purchased HW/steam in Proposed, the baseline shall also be modeled with Pursches HW/steam | Baseline | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No
144 | 18 | 144-18 | G3.1.1.3.4 | When a proposed desgin includes purchased heat all on-site distribution pumps shall be modeled in both the proposed design and base building design. | Baseline should include all on-site distribution pumps included int he Proposed design | For purchased HW/steam in Proposed, the baseline shall have the same number of pumps as proposed | Baseline | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No
147 | 19 | 147-19 | G3.1.2.2 | As- Designed | Plant capacities shall be based on coincident loads. | Plant sized based on coincident loads | Baseline | Baseline RMR = expected value | none | No
173 | 21 | 173-21 | G3.1.3.2 | As-Designed | When baseline building does not use purchased heat, baseline systems 1,5,7,11, 12 shall be modeled with natural draft boilers | Boilers should be modeled if baseline system = 1,5,7,11,12 and should be of natural draft type. | Baseline | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >0 | No
174 | 21 | 174-21 | G3.1.3.2 | As-Designed | When baseline building includes boilers model 2 equal sized boilers when conditioned floor area > 15,000 ft sized equally, otherwise model a single boiler. | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No
175 | 21 | 175-21 | G3.1.3.2 | As-Designed | When baseline building includes two boilers each shall stage as required by load. | For a baseline building with two boilers, each is staged based on Load. | Baseline | Baseline RMR = expected value | Number of boilers -= 2 | No
176 | 21 | 176-21 | G3.1.3.3 | As-Designed | When baseline building requires boilers, systems 1,5,7,11 and 12 - Model HWST = 180F and return design temp = 130F | HWST=180F, HSRT=130F | Baseline | Baseline RMR = expected value | none | No
177 | 21 | 177-21 | G3.1.3.4 | As-Designed | For systems 1,5,7,11 and 12 - HWST reset using OA reset schedule 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | HWST reset using OA reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | Baseline | Baseline RMR = expected value | none | No
178 | 21 | 178-21 | G3.1.3.5 | As-Designed | When baseline building includes boilers, Hot Water Pump Power = 19W/gpm | HW pump power = 19W/gpm | Baseline | Baseline RMR = expected value | none | No
179 | 21 | 179-21 | G3.1.3.5 | As-Designed | When the building uses boilers the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline | Baseline RMR = expected value | none | No
180 | 21 | 180-21 | G3.1.3.5 | As-Designed | When the system uses boilers the hot water system shall be modeled as primary only with continuous variable flow and a minimum turndown of 25%. | HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline | Baseline RMR = expected value | none | No
182 | 21 | 182-21 | G3.1.3.2 | As-Designed | When baseline building uses purchased heat, No boilers shall be modeled | For purchased HW system, no boilers shall be modeled. | Baseline | Baseline RMR = expected value | none | No
183 | 21 | 183-21 | G3.1.3.3 | As-Designed | When baseline building uses purchased HW baseline system hot water system shallbe modeled so - Model HWST = 180F and return design temp = 130F | For purchased HW system-HWST=180F, HWRT=130 F | Baseline | Baseline RMR = expected value | none | No
184 | 21 | 184-21 | G3.1.3.4 | As-Designed | When baseline building uses purchased heat do not model supply temperature reset. | For purchased HW system- No HWR modeled | Baseline | Baseline RMR = expected value | none | No
185 | 21 | 185-21 | G3.1.3.5 | As-Designed | When baseline building uses purchased heat hot water pump power = 14W/gpm | For purchased HW system, pump power = 14 W/gpm | Baseline | Baseline RMR = expected value | none | No
186 | 21 | 186-21 | G3.1.3.5 | As-Designed | When the building uses purchased heat the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | For purchased HW system- Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline | Baseline RMR = expected value | none | No
187 | 21 | 187-21 | G3.1.3.5 | As-Designed | When the building uses purchased heat the hot water system shall be modeled as primary only with continuous variable flow and a minimum turndown of 25%. | For purchased HW system - HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline | Baseline RMR = expected value | none | No

## Test Case Descriptions
App G Section ID | Rule ID | Test ID | Unique ID | Rule Description | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Test Scope | Test Description | RMR Tested | Expected Test Outcome | Test Outcome Text | Attribute Names (variables needed for test) | User RMR Value(s) | Proposed RMR Value(s) | Baseline RMR Value(s) | Test Case RMR Template | Note | Column1
Hot Water Boilers
139 | 18 | a | 139-18a | For purchased HW/steam in Proposed, the baseline shall also be modeled with Pursches HW/steam | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No | per Loop | Baseline RMR is modeled with purchased HW, same as proposed RMR | Baseline | Pass | Baseline RMR is modeled with purchased hot water | fluid_loops:loop_name fluid_loops:type hvac_systems:name hvac_systems:zones_served hvac_systems:hw_loop_name fluid_meter:name fluid_meter:type fluid_meter:loop_name |  | Purchased_HW_1 HW AHU_Pur-HW_System1 AHU_HW_System1 Zone 1, Zone 2 Purchased_HW_1 HW_meter_1 Purchased HW Purchased_HW_1 | Purchased_HW_1 HW AHU1 AHU1 Zone 1, Zone 2 Purchased_HW_1 HW_meter_1 Purchased HW Purchased_HW_1 |  | RCT would need to check the loop name, see if any boiler is attached to the loop. If not, check if any fluid meter for purchased HW is attached to the loop. Then make sure that the zones in the P-RMR with purchased HW are the same zones in B-PRM with purchased HW
139 | 18 | a | 139-18a | For purchased HW/steam in Proposed, the baseline shall also be modeled with Pursches HW/steam | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No | per Loop | Baseline RMR is not modeled with purchased HW | Baseline | Fail | Baseline RMR is not modeled with purchased hot water | fluid_loops:loop_name fluid_loops:type hvac_systems:name hvac_systems:zones_served hvac_systems:hw_loop_name fluid_meter:name fluid_meter:type fluid_meter:loop_name Boiler:Name Boiler:loop_name |  | Purchased_HW_1 HW AHU_Pur-HW_System1 AHU_HW_System1 Zone 1, Zone 2 Purchased_HW_1 HW_meter_1 Purchased HW Purchased_HW_1 | HW_1 HW AHU1 AHU1 Zone 1, Zone 3 HW_1 Boiler1 HW_1 |  | Note: Baseline might have multiple plant loops. Need to verify that the HVAC systems served by purchased CHW Plant loop in P-RMR are also served by purchsed chilled water in B-RMR In this test case, the zones are served by HW loop, but in the P-RMR the HW loop has a fluid meter (i.e. purchased HW), in the B-RMR has
144 | 18 | a | 144-18a | For purchased HW/steam in Proposed, the baseline shall have the same number of pumps as proposed | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No | per Loop | Baseline RMR is modeled purchased HW and with same number of pumps as proposed | Baseline | Pass | The purchased HW system in the Baseline RMR has the same number of pumps as proposed | fluid_loops:loop_name fluid_loops:type fluid_meter:name fluid_meter:type fluid_meter:loop_name pumps:name pump:loop_name |  | HW_1 HW HW_meter_1 Purchased HW HW_1 Pump1 HW_1 Pump2 HW_1 | HW_1 HW HW_meter_1 Purchased HW HW_1 Pump1 HW_1 Pump2 HW_1
144 | 18 | a | 144-18a | For purchased HW/steam in Proposed, the baseline shall have the same number of pumps as proposed | Baseline RMR = expected value | Proposed is modeled with purchased HW/steam | No | per Loop | Baseline RMR is modeled with purchased HW not modeled with same number of pumps as proposed | Baseline | Fail | The purchased HW system in the Baseline RMR does not have the same number of pumps as proposed | fluid_loops:loop_name fluid_loops:type fluid_meter:name fluid_meter:type fluid_meter:loop_name pumps:name pump:loop_name |  | HW_1 HW HW_meter_1 Purchased HW HW_1 Pump1 HW_1 Pump2 HW_2 | HW_1 HW HW_meter_1 Purchased HW HW_1 Pump1 HW_1 Pump2 HW_2 Pump3 HW_1
147 | 19 | a | 147-19a | Plant sized based on coincident loads | Baseline RMR = expected value | none | No | per Loop | Baseline RMR is modeled with a HW loop that is sized based on coincident loads | Baseline | Pass | Baseline HW loop has been sized on coincident loads | sizing_parameters:equipment_group sizing_parameters:equipment_name sizing_parameters:sizing_option |  |  | fluid_loops HW Loop 1 Coincident
147 | 19 | a | 147-19a | Plant sized based on coincident loads | Baseline RMR = expected value | none | No | per Loop | Baseline RMR is modeled with a HW loop that is not sized based on coincident loads | Baseline | Fail | Baseline HW loop has not been sized on coincident loads | sizing_parameters:equipment_group sizing_parameters:equipment_name sizing_parameters:sizing_option |  |  | fluid_loops HW Loop 1 Noncoincident
173 | 21 | a | 173-21a | Boilers should be modeled if baseline system = 1,5,7,11,12 and should be of natural draft type. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >0 | No | per Loop | Baseline RMR has a HW Loop with a natural draft boiler | Baseline | Pass | The boiler in the baseline RMR in HW Loop (Loop name) is of draft type "natural draft" | fluid_loops:name fluid_loops:type Boiler:name boiler:draft_type Boiler:loop_name |  |  | HW Loop 1 HW Boiler Gas Fired 1 Natural HW Loop 1 Boiler Gas Fired 2 Natural HW Loop 1 | Two Story Template | Boiler draft type is being determined through the baseline heating energy consumption. The baseline heating energy consumption should be all gas, electric energy consumption would indicate fan energy consumption for a forced draft boiler However, this doesnt work if any space meets exceptions and is modeled with system 3 or 4.
173 | 21 | b | 173-21b | Boilers should be modeled if baseline system = 1,5,7,11,12 and should be of natural draft type. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >0 | No | per Loop | Baseline RMR has a HW Loop with a natural draft boiler | Baseline | Fail | The boiler in the baseline RMR in HW Loop (Loop name) is not of draft type "natural draft" | fluid_loops:name fluid_loops:type Boiler:name boiler:draft_type Boiler:loop_name |  |  | HW Loop 1 HW Boiler Gas Fired 1 Natural HW Loop 1 Boiler Gas Fired 2 Forced HW Loop 1 | Two Story Template | Boiler draft type is being determined through the baseline heating energy consumption. The baseline heating energy consumption should be all gas, electric energy consumption would indicate fan energy consumption for a forced draft boiler
174 | 21 | a | 174-21a | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with a single boiler | Baseline | Pass | There is a single boiler in the baseline RMR in HW Loop (Loop name) as expected | fluid_loops:name fluid_loops:type Boiler:name Boiler:loop_name Boiler:design_capacity HVAC_Systems:name HVAC_Systems:hw_loop_name Zone:name Zone:area Zone:hvac_system_name |  |  | HW Loop 1 HW Boiler HW Loop 1 400,000 Btu/hr AHU 1 HW Loop 1 Office Zone 1 4000 ft2 AHU 1 Office Zone 2 4000 ft2 AHU 1 | Two Story Template | RCT will have to look up the total ar ea served by the hot water loop to fcevaluate this rule.S5 hsrgfg yetfgfgtrfscsewaxzxdxcms
174 | 21 | b | 174-21b | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with a single boiler | Baseline | Fail | There are two boilers in the baseline RMR in HW Loop (Loop name) where one is expected. | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name boiler:design_capacity |  |  | HW Loop 1 Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 12,000ft2 Boiler Gas Fired 1 400,000 Btu/hr Boiler Gas Fired 2 400,000 Btu/hr | Two Story Template | RCT will have to look up the total area served by the hot water loop to evaluate this rule.
174 | 21 | c | 174-21c | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with a single boiler | Baseline | Pass | There is a single boiler in the baseline RMR in HW Loop (Loop name) as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name boiler:design_capacity |  |  | HW Loop 1 Boiler Boiler Gas Fired 1 12,000ft2 Boiler Gas Fired 1 400,000 Btu/hr | Two Story Template | RCT will have to look up the total area served by the hot water loop to evaluate this rule.
174 | 21 | d | 174-21d | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with a single boiler | Baseline | Fail | There are two boilers in the baseline RMR in HW Loop (Loop name) where one is expected. | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name boiler:design_capacity |  |  | HW Loop 1 Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 12,000ft2 Boiler Gas Fired 1 400,000 Btu/hr Boiler Gas Fired 2 400,000 Btu/hr | Two Story Template
174 | 21 | e | 174-21e | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with two equally sized boilers | Baseline | Pass | There are two equally sized boilers in the baseline RMR in HW Loop (Loop name) as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name boiler:design_capacity |  |  | HW Loop 1 Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 18,000ft2 Boiler Gas Fired 1 400,000 Btu/hr Boiler Gas Fired 2 400,000 Btu/hr | Five Story Template
174 | 21 | f | 174-21f | For building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler should be modeled. | Baseline RMR = expected value | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | No | per Loop | Baseline RMR has a HW Loop with two equally sized boilers | Baseline | Fail | There are three boilers in the baseline RMR in HW Loop (Loop name) where two equally sized boilers were expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name boiler:design_capacity |  |  | HW Loop 1 Boiler Boiler Gas Fired 1, Boiler Gas Fired 2, Boiler Gas Fired 3 18,000ft2 Boiler Gas Fired 1 300,000 Btu/hr Boiler Gas Fired 2 300,000 Btu/hr Boiler Gas Fired 3 300,000 Btu/hr | Five Story Template
175 | 21 | a | 175-21a | For a baseline building with two boilers, each is staged based on Load. | Baseline RMR = expected value | Number of boilers -= 2 | No | per Loop | Baseline RMR has a HW Loop with two boilers staged based on load | Baseline | Pass | There are two boilers in the baseline RMR in HW Loop (Loop name) which have been staged based on load | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name Boiler:design_capacity Boiler:operation_lower_limit Boiler_operation_upper_limit |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 Boiler Gas Fired 1 35 kBtu/hr 0 kBtu/hr 35 kBtu/hr Boiler Gas Fired 2 35 kBtu/hr 35 kBtu/hr 70 kBtu/hr | Five Story Template | PRMR RM States - Software shall bring the first boiler to 100% capacity prior to taging of the next boiler. RCT can verify this by 1. Verifying boiler energy use : they should not be equal 2. Calculate 'Realized Annual Efficiency' or ratio of Annual Load to Annual Energy Use. Values significantly lower than boiler efficiency would be a flag. 3. Can also ask for boiler lower and upper limit for operation. The second boiler should use the upper limit of the first boiler as its lower limit. Annual load is not something tools might be able to provide (E+ can only provide this if an ideal loads system is added), so will add a test based on #3
175 | 21 | b | 175-21b | For a baseline building with two boilers, each is staged based on Load. | Baseline RMR = expected value | Number of boilers -= 2 | No | per Loop | Baseline RMR has a HW Loop with two boilers staged based on load | Baseline | Fail | There are boilers in the baseline RMR in HW Loop (Loop name) which have not been staged based on load | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:area_served Boiler:name Boiler:design_capacity Boiler:operation_lower_limit Boiler_operation_upper_limit |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 Boiler Gas Fired 1 35 kBtu/hr 0 kBtu/hr 70 kBtu/hr Boiler Gas Fired 2 35 kBtu/hr 0 kBtu/hr 70 kBtu/hr | Five Story Template | Here both boilers could come on at the same time to meet the heating load which would result in higher boiler energy consumption due to part load performance. This is incorrect.
176 | 21 | a | 176-21a | HWST=180F, HSRT=130F | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, where HWST=180F and HWRT = 130F | Baseline | Pass | The HWST and HWRT in the baseline RMR in HW Loop (Loop name) is as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:design_supply_temperature fluid_loops:design_return_temperature |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 180 F 130 F | Five Story Template
176 | 21 | b | 176-21b | HWST=180F, HSRT=130F | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, where HWST=180F and HWRT = 130F | Baseline | Fail | The HWST and HWRT in the baseline RMR in HW Loop (Loop name) is not as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:design_supply_temperature fluid_loops:design_return_temperature |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 175 F 125 F | Five Story Template
177 | 21 | a | 177-21a | HWST reset using OA reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HWST is reset based on OAT (HWST=180F at 20F OA DryBylb, HWST=150F at 50F OA B=DryBulb, ramped linearly inbetween) | Baseline | Pass | The HWST has been reset based on OAT in the baseline RMR in HW Loop (Loop name) is as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:temperature_reset_type fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:loop_supply_temp_at_outdoor_high fluid_loops:loop_supply_temp_at_outdoor_low |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 outdoor air temperature reset 50F 20F 150F 180F | Five Story Template
177 | 21 | b | 177-21b | HWST reset using OA reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HWST is reset based on OAT (HWST=180F at 20F OA DryBylb, HWST=150F at 50F OA B=DryBulb, ramped linearly inbetween) | Baseline | Fail | The HWST has not been reset based on OAT in the baseline RMR in HW Loop (Loop name) as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:temperature_reset_type fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:loop_supply_temp_at_outdoor_high fluid_loops:loop_supply_temp_at_outdoor_low |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 outdoor air temperature reset 50F 20F 140F 180F | Five Story Template
177 | 21 | c | 177-21c | HWST reset using OA reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HWST is reset based on OAT (HWST=180F at 20F OA DryBylb, HWST=150F at 50F OA B=DryBulb, ramped linearly inbetween) | Baseline | Pass | The HWST has been reset based on OAT in the baseline RMR in HW Loop (Loop name) is as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:temperature_reset_type fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:outdoor_high_for_loop_supply_temp_reset fluid_loops:loop_supply_temp_at_outdoor_high fluid_loops:loop_supply_temp_at_outdoor_low |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 none | Five Story Template
178 | 21 | a | 178-21a | HW pump power = 19W/gpm | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop pump power = 19W/GPM | Baseline | Pass | The HW loop pump power in HW Loop (Loop name) is as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pumps:power pump:design_flow |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 5 kW 263.15 GPM | Five Story Template
178 | 21 | b | 178-21b | HW pump power = 19W/gpm | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop pump power = 19W/GPM | Baseline | Pass | The HW loop pump power in HW Loop (Loop name) is as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pump:design_flow pumps:head pumps:motor_eff pumps:impeller_eff |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 1 GPM 60 ft 90% 66.67% | Five Story Template
178 | 21 | c | 178-21c | HW pump power = 19W/gpm | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop pump power = 19W/GPM | Baseline | Fail | The HW loop pump power in HW Loop (Loop name) is not as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pumps:power pump:design_flow |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 5 kW 220 GPM | Five Story Template
179 | 21 | a | 179-21a | Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop serves 12,000 ft2. Pump modeled as riding the pump curve | Baseline | Pass | The HW loop pump in HW Loop (Loop name) has been modeled as fixed speed, variable flow (pump riding the pump curve), as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loop:hvac_systems_served fluid_loops:pump_name hvac_system:name have_system:zones_served zone:name zone:area pmps:name pump:speed pump:flow_control |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 AHU_VAV-RH_1 HW Pump 1 AHU_VAV-RH_1 Zone 1, Zone 2 Zone 1 60,000 ft2 Zone 2 40,000 ft2 HW Pump 1 fixed speed variable flow Fixed Speed Variable Flow | Five Story Template
179 | 21 | b | 179-21b | Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop serves 12,000 ft2. Pump modeled as riding the pump curve | Baseline | Fail | The HW loop pump in HW Loop (Loop name) has not been modeled with fixed speed, variable flow (pump riding the pump curve) | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loop:hvac_systems_served fluid_loops:pump_name hvac_system:name have_system:zones_served zone:name zone:area pmps:name pump:speed pump:flow_control |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 AHU_VAV-RH_1 HW Pump 1 AHU_VAV-RH_1 Zone 1, Zone 2 Zone 1 60,000 ft2 Zone 2 40,000 ft2 HW Pump 1 fixed speed constant flow | Five Story Template
179 | 21 | c | 179-21c | Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop serves 150,000 ft2. Pump modeled as variable speed, variable flow | Baseline | Pass | The HW loop pump in HW Loop (Loop name) has been modeled as variable speed, variable flow , as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loop:hvac_systems_served fluid_loops:pump_name hvac_system:name have_system:zones_served zone:name zone:area pmps:name pump:speed pump:flow_control |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 AHU_VAV-RH_1 HW Pump 1 AHU_VAV-RH_1 Zone 1, Zone 2 Zone 1 60,000 ft2 Zone 2 40,000 ft2 HW Pump 1 variable speed variable flow | Five Story Template
179 | 21 | d | 179-21d | Area serverd >=120,000 ft2, Pump is modeled with VSD Area served <120.000 ft2, pump modeled as riding the pump curve. | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW Loop serves 150,000 ft2. Pump modeled as riding the pump curve | Baseline | Fail | The HW loop pump in HW Loop (Loop name) has not been modeled as variable speed, variable flow , as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loop:hvac_systems_served fluid_loops:pump_name hvac_system:name have_system:zones_served zone:name zone:area pmps:name pump:speed pump:flow_control |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 AHU_VAV-RH_1 HW Pump 1 AHU_VAV-RH_1 Zone 1, Zone 2 Zone 1 60,000 ft2 Zone 2 40,000 ft2 HW Pump 1 fixed speed constant flow | Five Story Template
180 | 21 | a | 180-21a | HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW pump is primary only | Baseline | Pass | The HW loop Pump has been modeled as primary only, as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pump:type |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 Primary | Five Story Template
180 | 21 | b | 180-21b | HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, HW pumps are primary, secondary | Baseline | Fail | The HW loop pump has not be modeled as Primary Only, which is not as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pump:type |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1, HW Pump 2 HW Pump 1 Primary HW Pump 2 Secondary | Five Story Template
180 | 21 | c | 180-21c | HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, boiler turndown ratio is 25% | Baseline | Pass | Pump serving the HW Loop has a minimum flow of of 25%, as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pump:minimum_flow_ratio |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 0.25 | Five Story Template
180 | 21 | d | 180-21d | HW Loop is modeled as primary only, with continuous variable flow. Min turndown= 25% | Baseline RMR = expected value | none | No | per Loop | Baseline RMR has HW loop with Boiler, boiler turndown ratio is 15% | Baseline | Fail | Pump serving the HW Loop does not have a minimum flow of of 25%, as expected | fluid_loops:name fluid_loops:plant_equipment_typelist fluid_loops:plant_equipment_namelist fluid_loops:pump_name pmps:name pump:minimum_flow_ratio |  |  | HW Loop 1 Boiler, Boiler Boiler Gas Fired 1, Boiler Gas Fired 2 HW Pump 1 HW Pump 1 0.15 | Five Story Template

## Schema Data Elements
Data_Group | Attribute Names (variables needed for test) | Std 229 Schema Name | Description | Units | Type | Enumerations
sizing_parameters | equipment_group |  | type of equipment for which the sizing parameters are defined |  | list | enumeration of fluid_loop, hvac_system
sizing_parameters | equipment_name |  | Name of equipment for which the sizing parameters are defined | none | String
sizing_parameters | sizing_option |  |  | none | list | coincident, noncoincident
fluid_loops | name |  | HW Loop name | none | String
fluid_loops | type |  | Type of loop | none | Enumeration | HW
fluid_loops | design_supply_temperature |  | Design Supply Temperature | degrees F | Number
fluid_loops | design_return_temperature |  | Design Return Temperature | degrees F | Number
fluid_loops | temperature_reset_type |  | Type of temperature reset used by loop | none | Value List | No Reset, constant, OA_Reset, Load_Reset, Other
fluid_loops | outdoor_high_for_loop_supply_temp_reset |  |  | degrees F | Number
fluid_loops | outdoor_low_for_loop_supply_temp_reset |  |  | degrees F | Number
fluid_loops | loop_supply_temp_at_outdoor_high |  |  | degrees F | Number
fluid_loops | loop_supply_at_outdoor_low |  |  | degrees F | Number
fluid_loops | peak_heating_capacity |  | Design capacity | kWh | Number
Pumps | name |  | Name identifying pump | none | String | Unique name for pump on a loop
Pumps | type |  | Primary, Secondary or Distribution Pump | List | String | Enumeration for 'Primary', 'Secondary', 'Distribution' | remove this. BEM tool cannot identify if a pump is P or S.
Pumps | power |  | Pump power | kW | Number
Pumps | speed |  | Options for pump control | List | String | Enumerations for- Fixed speed, Two Speed, Variable Speed
Pumps | flow_control |  | Flow control options | List | String | Enumerations for 'Fixed flow', 'Variable Flow'
Pumps | minimum_flow_fraction |  | Minimum pump flow turndown as a percentage of design flow | % | Number
Pumps | design_flow |  | Design Pump Flowrate | gpm or L/s | Number
Pumps | loop_name | [5 empty] | RCT will need to check which loop the pump has been assigned to to verify if a
Pumps | has_vfd |  |  | none | Boolean | Used to identify if the loop is continuous flow
Boilers | name |  | Boiler name | none | String
Boilers | design_capacity |  | heating capacity | btu/hr | Number
Boilers | draft_type |  |  | none | enumeraton | forced, natural
Boilers | Operation-Lower Limit |  | Heating load range operation, lower limit | btu/hr | Number
Boilers | Operation- Upper Limit |  | Heating load range operation, upper limit | btu/hr | Number
Boilers | loop_name
HVAC Systems | name |  |  | none | String
HVAC_Systems | Zones served |  |  | none | List
HVAC_Systems | hw_loop_name |  |  | none | String
HVAC_Systems | chw_loop_name |  |  | none | String
HVAC_Systems | cw_loop_name |  |  | none | String
HVAC_Systems | preheat_loop_name |  |  | none | String
HVAC_Systems | reheat_loop_name |  |  | none | String
Zone | name |  | name of thermal zone | none | string
Zone | area |  | area of thermal zone | ft2 | Number
fluid_meters | name
fluid_meters | type |  |  |  |  | CHW, HW
fluid_meters | loop_name

## PumpCalcs
bhp = gpm*hd/(3960*imp. Eff)
| W= gpm*hd/(3960*imp. Eff)*(746/mot eff) |  | ft_to_Pa | 2989.089
W= gpm*hd/(3960*imp. Eff * mot eff)*746
hd=W/(gpm/(gpm/(3960*imp eff*mot eff)*746)
ECB
| gpm | 1
| Head (Pa) | 179345.34
| Head (ft) | 60
| mot eff | 0.9
| imp eff | 66.67
| bhp | 0.00022726
| W/gpm | 0.18837
| Comb mot and imp eff. | 60.003
| Calculation Steps |  | 178208
1 | Assume motor efficiency of 0.9
2 | Assume Impeller Efficiency of 0.78
3 | Pump Power/GPM is the user input which will be used.
4 | Use equation below to calculate Pump Head (ft of H2O)
5 | Convert pump head to Pa
Test
For Pump Power/GPM of 16 W/GPM, the pump head is 59.6 ft.
𝑃𝑢𝑚𝑝 𝐻𝑒𝑎𝑑(𝑓𝑡)=(𝑃𝑢𝑚𝑝𝑃𝑜𝑤𝑒𝑟/𝐺𝑃𝑀 ∗𝑀𝑜𝑡𝑜𝑟 𝐸𝑓𝑓𝑖𝑐𝑖𝑒𝑛𝑐𝑦 ∗"Impeller Eff ∗ 3960 " )/746=