## Rules
App G Section ID | Rule ID | Rule Description | Applicable RMR | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Note | Complexity | Importance | Triggers
| 1 | Design CHW Loop Supply Temperature = 44F | Baseline | Baseline RMR = expected value | none | No
| 2 | Design CHW Loop Return Temperature = 56F | Baseline | Baseline RMR = expected value | none | No
| 3 | CHW Loop temperature reset = OA Reset | Baseline | Baseline RMR = expected value | none | No
| 4 | CHW Loop temepratrue reset schedule values are correct. | Baseline | Baseline RMR = expected value | none | No | Test required OA reset temperature values
| 5 | CHW Loop temperature reset = Load Reset when it serves an AHU of System Type 11. | Baseline | Baseline RMR = expected value | none | No
| 6 | CHW Loop Max reset Temp is 54F when Rule 5 is true | Baseline | Baseline RMR = expected value | rule 5 is True | No
| 7 | CHW Loop has a secondary pump | Baseline | Baseline RMR = expected value | none | No
| 8 | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline | Baseline RMR = expected value | rule 8 is true | No
| 9 | Secondary pump min flow setpoint is 25% when rule 8 | Baseline | Baseline RMR = expected value | none | No
| 10 | Secondary pump speed control = ride curve when loop capacity < 300 tons | Baseline | Baseline RMR = expected value | none | No
| 11 | Secondary pump power = 13W/gpm | Baseline | Baseline RMR = expected value | none | No
| 12 | Purchased CHW Loop temp reset = none | Baseline | Baseline RMR = expected value | none | No
| 13 | Purchased CHW loop has a distribution pump (T/F) | Baseline | Baseline RMR = expected value | none | No
| 14 | Distribution pump speed control is a VFD | Baseline | Baseline RMR = expected value | Rule 13 is true | No
| 15 | Distribution pump minimum flow setpoint = 25% | Baseline | Baseline RMR = expected value | Rule 13 is true | No
| 16 | Distribution pump power is 16W/gpm | Baseline | Baseline RMR = expected value | Rule 13 is true | No
| 17 | Heat Rejection loop has a single heat rejection device attached? (T/F) | Baseline | Baseline RMR = expected value | none | Yes
| 18 | Heat Rejection device type = axial fan | Baseline | Baseline RMR = expected value | Rule 17 is true | Yes
| 19 | Heat rejection Device Range = 10 degrees | Baseline | Baseline RMR = expected value | Rule 17 is true | No
| 20 | Design Wet Bulb is 12.8C<=WB<=32.2C? (55F->90F) | Baseline | Baseline RMR = expected value | Rule 17 is true | Yes
| 21 | Heat Rejection Device Approach calaculated correctly (T/F) | Baseline | Baseline RMR = expected value | Rule 36 is true | No
| 22 | Heat Rejection Design Supply Temperature is correct | Baseline | Baseline RMR = expected value | Rule 36 is true | No | use formula 25.72-(.24 x design WB)
| 23 | Heat Rejection fan power = 3.47 L/s-kW (38.2 gpm/hp) | Baseline | Baseline RMR = expected value | Rule 36 is true | No | Design Wetbulb + approach
| 24 | Heat Rejection fan speed control = VFD? | Baseline | Baseline RMR = expected value | Rule 36 is true | No
| 25 | Heat Rejection Loop temperature reset = Load Reset | Baseline | Baseline RMR = expected value | none | No
| 26 | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline | Baseline RMR = expected value | Rule 23 is true | Yes | Lookup min reset temp
| 27 | Chiller Type is correct per Table G3.1.3.7? | Baseline | Baseline RMR = expected value | none | Yes | Lookup chiller type
| 28 | Chiller efficiency is correct per Table G3.5.3 | Baseline | Baseline RMR = expected value | none | Yes | Lookup chiller efficiency
| 29 | Chiller has an associated primary pump? | Baseline | Baseline RMR = expected value | none | No
| 30 | Primary pump sepeed control = constant | Baseline | Baseline RMR = expected value | rule 27 is true | No
| 31 | Primary pump power = 9W/gpm | Baseline | Baseline RMR = expected value | Rule 27 is true and Loop doesn't serve System 11 | No
| 32 | Primary pump power = 12W/gpm | Baseline | Baseline RMR = expected value | Rule 27 is true and Loop serves system 11 | No
| 33 | Chiller has an associated condenser pump? | Baseline | Baseline RMR = expected value | none | No
| 34 | Condenser pump speed control = constant | Baseline | Baseline RMR = expected value | Rule 31 is true | No
| 35 | Condenser pump power is 19W/gpm | Baseline | Baseline RMR = expected value | Rule 31 is true and loop does not serve system type 11 | No
| 36 | Distribution pump power is 22W/gpm | Baseline | Baseline RMR = expected value | Rule 31 is true and loop serves system type 11 | No
| 37 | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline | Baseline RMR = expected value | none | Yes | calculate correct number of chillers | <300 = 1scrw, 300-600 2scrw, 600-1600 2cent, >1600 cap/800 cent
| 38 | Chiller capacity is correct | Baseline | Baseline RMR = expected value | Rule 37 is true | Yes
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on H31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Schema Data Elements
Data_Group | Attribute Names (variables needed for test) | Std 229 Schema Name | Description | Units | Type | Enumerations
Hydronic_Loops | name |  | Loop Name | none | Text
Hydronic_Loops | type |  | Type of Loop - | none | Value List | CHW, purchased_CHW, Heat_rejection,
Hydronic_Loops | design_flow |  | Design Flow Rate of Loop | gpm or L/s | Number
Hydronic_Loops | design_supply_temperature |  | Design Supply Temperature | degrees C | Number
Hydronic_Loops | design_return_temperature |  | Design Return Temperature | degrees C | Number
Hydronic_Loops | temperature_reset_type |  | Type of temperature reset used by loop | none | Value List | constant, OA_Reset, Load_Reset, Other
Hydronic_Loops | outdoor_air_reset_schedule_name |  | Outdoor Air reset Schedule Name | none | Text | Name of schedule used for OA Reset.
Hydronic_Loops | minimum_reset_temeprature |  | Minimum Loop temperature Reset Setpoint | degrees C | Number
Hydronic_Loops | heat_rejection_name(s) |  | Attached Heat Rejection Devices | none | Array | Names of attached heat rejection devices
Hydronic_Loops | chiller_name(s) |  | Attached Chillers | none | Array | Names of Attached Chillers
Hydronic_Loops | secondary_pump_name |  | Associated secondary pump | none | Text | Name of associated secondary pump
Hydronic_Loops | distribution_pump_name |  | associated distribution pump | none | text | Name of associated distribution pump
Hydronic_loops | HVAC_systems_served_name |  | name of HVAC systems served by loop | none | array | names of HVAC systems served by loop
Hydronic_Loops | peak_cooling_capacity |  | Design capacity | kWh | value
Pumps | name |  | Pump Name
Pumps | type |  | Type of Pump | none | Value | primary_CHW, secondary_CHW, distribution_CHW, condenser
Pumps | power |  | Pump power in kW | kW | Number
Pumps | speed_control |  | Method fo speed control | none | Value | constant, ride_curve, VFD, 2-speed
Pumps | minimum_flow_fraction |  | Minimum pump flow turndown as a percentage of design flow | % | Value
Pumps | design_flow |  | Design Pump Flowrate | gpm or L/s | Value
Pumps | loop_name |  | Name of loop pump is attached to. | none | Text
Chiller | name |  | Chiller Name | none | Text
Chiller | type |  | Chiller Type | none | Value | Screw, centrifugal, other
Chiller | design_capacity |  | Chiller Design Cooling Capacity | kW | Number
Chiller | design_flow_evaporatpr |  | Chiller evaporator design flow | L/s | Number
Chiller | design_flow_condenser |  | Chiller condenser design flow | L/s | Number
Chiller | full_load_efficiency |  | Full Low Efficiency (COP) | COP | Number
Chiller | loop_name |  |  | none | String
Chiller | primary_pump_name |  | Name of attached primary pump | none | Text
Chiller | condenser_pump_name |  | Name of attached condenser pump | none | Text
Chiller | cooling_loop_name |  | Name of cooling loop | none | Text
Chiller | heat_rejection_loop_name |  | Name of heat rejection loop | none | Text
heat_rejection | name |  | Heat Rejection Device Name | none | Text
heat_rejection | type |  | Heat Rejection Type | none | Value | axial-fan, centrifugal, dry-cooler, evaporative, other
heat_rejection | range |  | Heat rejection Range | degrees C | Number
heat_rejection | approach |  | Heat rejection Approach | degrees C | Number
heat_rejection | reset_type |  | Leaving Temperature reset strategy | none | Value | constant, load_reset, other
heat_rejection | minimum_reset_temperature |  | Minimum leavinng temperature setpoint | degrees C | Number
heat_rejection | fan_power |  | Fan Power | kW | Number
heat_rejection | fan_speed_control |  | Fan Speed Control Type | none | Value | constant, 2-speed, VFD, other
heat_rejection | design_supply_temperature |  | Design leaving water temperature | degrees C | Number
heat_rejection | design_wetbulb_temperature |  | Design wetbulb temperature 0.4%ASHRAE MCWB | degrees C | Number
heat_rejection | design_water_flowrate |  | Design condenser water flow rate | L/s | Number
building | ASHRAE_climate_zone |  | ASHRAE Climate Zone | none | value | 0A,0B,1A,1B,2A,2B,3A,3B,3C,4A,4B,4C,5A,5B,5C,6A,6B,7,8
RCT calculated attributes required for RCT tests
Hydronic_Loops | serves_System_Type_11 |  | Flag whether loop serves System 11 | none | binary
fluid_meters | name
fluid_meters | type |  |  |  |  | CHW, HW
fluid_meters | loop_name
Note on D22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Test Case Descriptions
App G Section ID | Rule ID | Test ID | Unique ID | Rule Description | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Test Scope | Test Description | RMR Tested | Expected Test Outcome | Test Outcome Text | Attribute Names (variables needed for test) | User RMR Value(s) | Proposed RMR Value(s) | Baseline RMR Value(s) | Test Case RMR Template | Note | Units used for TCD
DISTRIBUTION TRANSFORMERS
G3 | 1 | a | G3-1a | Design CHW Loop Supply Temperature = 44F | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Supply Temperature equals 44 in Baseline RMR | Baseline | Pass | Baseline CHW Loop Supply Temperature is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:design_supply_temperature |  |  | CHW_Loop_1 CHW 6.7 | One Story Template |  | SI
G3 | 1 | b | G3-1b | Design CHW Loop Supply Temperature = 44F | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Supply Temperature does not equal 44 in Baseline RMR | Baseline | Fail | Baseline CHW Loop Supply Temperature should be 44F | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:design_supply_temperature |  |  | CHW_Loop_1 CHW 5.6 | One Story Template |  | SI
G3 | 2 | a | G3-2a | Design CHW Loop Return Temperature = 56F | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Return Temperature equals 56 in Baseline RMR | Baseline | Pass | Baseline CHW Loop Return Temperature is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:design_return_temperature |  |  | CHW_Loop_1 CHW 13.3 | One Story Template |  | SI
G3 | 2 | b | G3-2b | Design CHW Loop Return Temperature = 56F | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Return Temperature does not equal 56 in Baseline RMR | Baseline | Fail | Baseline CHW Loop Return Temperature should be 56F | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:design_return_temperature |  |  | CHW_Loop_1 CHW 11.1 | One Story Template |  | SI
G3 | 3 | a | G3-3a | CHW Loop temperature reset = OA Reset | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Temperature Reset Type equals "OA Reset" | Baseline | Pass | Baseline CHW Loop Temperature Reset Type is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type |  |  | CHW_Loop_1 CHW OA_reset | One Story Template
G3 | 3 | b | G3-3b | CHW Loop temperature reset = OA Reset | Baseline RMR = expected value | none | No | Per Loop | CHW Loop Temperature Reset Type does not equal "OA Reset" | Baseline | Fail | Baseline CHW Loop Temperature Reset Type should be OA Reset. | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type |  |  | CHW_Loop_1 CHW none | One Story Template
G3 | 4 | a | G3-4a | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR = expected value | none | No | Per Loop | OA Reset Schedule values are correct | Baseline | Pass | Baseline CHW Loop OA Reset Schedule values are correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:outdoor_air_reset_schedule_name |  |  | CHW_Loop_1 CHW CHW_OA_Schedule | One Story Template | These tests are not finished. Need to figure out best way to test schedule
G3 | 4 | b | G3-4b | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR = expected value | none | No | Per Loop | OA Reset Schedule values are not correct | Baseline | Fail | Baseline CHW OA Reset Schedule values are not correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:outdoor_air_reset_schedule_name |  |  | CHW_Loop_1 CHW CHW_OA_Schedule | One Story Template
G3 | 4 | c | G3-4c | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR = expected value | none | No | Per Loop | OA Reset Schedule values are not correct | Baseline | Fail | Baseline CHW OA Reset Schedule values are not correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:outdoor_air_reset_schedule_name |  |  | CHW_Loop_1 CHW CHW_OA_Schedule | One Story Template
G3 | 4 | d | G3-4d | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR = expected value | none | No | Per Loop | OA Reset Schedule values are not correct | Baseline | Fail | Baseline CHW OA Reset Schedule values are not correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:outdoor_air_reset_schedule_name |  |  | CHW_Loop_1 CHW CHW_OA_Schedule | One Story Template
G3 | 4 | e | G3-4e | CHW Loop temepratrue reset schedule values are correct. | Baseline RMR = expected value | none | No | Per Loop | OA Reset Schedule values are not correct | Baseline | Fail | Baseline CHW OA Reset Schedule values are not correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:outdoor_air_reset_schedule_name |  |  | CHW_Loop_1 CHW CHW_OA_Schedule | One Story Template
G3 | 5 | a | G3-5a | CHW Loop temperature reset = Load Reset when it serves an AHU of System Type 11. | Baseline RMR = expected value | none | No | Per Loop | CHW Temperature Rest equals Load Reset when System 11 is used | Baseline | Pass | Baseline CHW Loop temperature reset type is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type hydronic_loops:serves_system_type_11 |  |  | CHW_Loop_1 CHW load_reset True | One Story Template | These tests only get used if Serves_system_type_11 is true
G3 | 5 | b | G3-5b | CHW Loop temperature reset = Load Reset when it serves an AHU of System Type 11. | Baseline RMR = expected value | none | No | Per Loop | CHW Temperature Rest does not equal Load Reset when System 11 is used | Baseline | Fail | Baseline CHW Loop temperature reset type should equal load reset because System 11 is included in Baseline RMR. | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type hydronic_loops:serves_system_type_11 |  |  | CHW_Loop_1 CHW none True | One Story Template
G3 | 6 | a | G3-6a | CHW Loop Max reset Temp is 54F when Rule 5 is true | Baseline RMR = expected value | rule 5 is True | No | Per Loop | CHW Loop Maximum Reset Temperature equals 54F | Baseline | Pass | Baseline CHW Loop Maximum Reset Temperature is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:minimum_reset_temperature hydronic_loops:serves_system_type_11 |  |  | CHW_Loop_1 CHW 12.2 True | One Story Template | These tests only get used if Serves_system_type_11 is true | SI
G3 | 6 | b | G3-6b | CHW Loop Max reset Temp is 54F when Rule 5 is true | Baseline RMR = expected value | rule 5 is True | No | Per Loop | CHW Loop Maximum Reset Temperature does not equal 54F | Baseline | Fail | Baseline CHW Loop Maximum Reset Temperature should be 54F | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:minimum_reset_temperature hydronic_loops:serves_system_type_11 |  |  | CHW_Loop_1 CHW 10 True | One Story Template |  | SI
G3 | 7 | a | G3-7a | CHW Loop has a secondary pump | Baseline RMR = expected value | none | No | Per Loop | CHW Loop has an associated secondary pump | Baseline | Pass | Baseline CHW Loop has an associated secondary pump | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary | One Story Template
G3 | 7 | b | G3-7b | CHW Loop has a secondary pump | Baseline RMR = expected value | none | No | Per Loop | CHW Loop does not have an associated secondary pump | Baseline | Fail | Baseline CHW Loop does not have an associated secondary pump | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 distribution | One Story Template
G3 | 7 | c | G3-7c | CHW Loop has a secondary pump | Baseline RMR = expected value | none | No | Per Loop | CHW Loop does not have an associated secondary pump | Baseline | Fail | Baseline CHW Loop does not have an associated secondary pump | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type |  |  | CHW_Loop_1 CHW null SCHW_Pump_1 secondary | One Story Template
G3 | 8 | a | G3-8a | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline RMR = expected value | rule 8 is true | No | Per Pump | Secondary pump speed control equals VFD, design capacity > 300 tons | Baseline | Pass | Baseline CHW Loop secondary pump speed control is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 400 | One Story Template |  | IP
G3 | 8 | b | G3-8b | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline RMR = expected value | rule 8 is true | No | Per Pump | Secondary pump speed control equals VFD, design capacity =300 tons | Baseline | Pass | Baseline CHW Loop secondary pump speed control is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 300 | One Story Template |  | IP
G3 | 8 | c | G3-8c | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline RMR = expected value | rule 8 is true | No | Per Pump | Secondary pump speed control does not equal VFD | Baseline | Fail | Baseline CHW Loop Secondary pump speed control should be VFD | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary none 400 | One Story Template |  | IP
G3 | 8 | d | G3-8d | Secondary Pump speed control = VFD when loop capacity >=300 tons | Baseline RMR = expected value | rule 8 is true | No | Per Pump | Secondary pump speed control equals VFD, loop cooling capacity <300 tons | Baseline | Fail | Baseline CHW Loop Secondary pump speed control should be ride curve | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 250 | One Story Template |  | IP
G3 | 9 | a | G3-9a | Secondary pump min flow setpoint is 25% when rule 8 | Baseline RMR = expected value | none | No | Per Pump | Secondary pump minimum speed setpoint equals 25% when a VFD is used. | Baseline | Pass | Baseline CHW Loop Secondary pump minimum speed setpoint is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:minimum_flow_fraction |  |  | CHW_Loop_1 CHW null SCHW_Pump_1 secondary 0.25 | One Story Template
G3 | 9 | b | G3-9b | Secondary pump min flow setpoint is 25% when rule 8 | Baseline RMR = expected value | none | No | Per Pump | Secondary pump minimum speed setpoint does not equal 25% when a VFD is used. | Baseline | Fail | Baseline CHW Loop Secondary pump minimum speed setpoint should be 25% | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:minimum_flow_fraction |  |  | CHW_Loop_1 CHW null SCHW_Pump_1 secondary 0.4 | One Story Template
G3 | 10 | a | G3-10a | Secondary pump speed control = ride curve when loop capacity < 300 tons | Baseline RMR = expected value | none | No | Per Pump | Secondary pump speed control equals "ride cuirve" | Baseline | Pass | Baseline CHW Loop Secondary pump speed control is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 250 | One Story Template |  | IP
G3 | 10 | b | G3-10b | Secondary pump speed control = ride curve when loop capacity < 300 tons | Baseline RMR = expected value | none | No | Per Pump | Secondary pump speed control does not equal "ride curve" | Baseline | Fail | Baseline CHW Loop Secondary pump speed control should be "ride curve" | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 250 | One Story Template |  | IP
G3 | 10 | b | G3-10b | Secondary pump speed control = ride curve when loop capacity < 300 tons | Baseline RMR = expected value | none | No | Per Pump | Secondary pump speed control equals "riode curve" , loop capacity > 300 tons | Baseline | Fail | Baseline CHW Loop Secondary pump speed control should be "VFD" | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:speed_control hydronic_loops:peak_cooling_capacity |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary VFD 250 | One Story Template |  | IP
G3 | 11 | a | G3-11a | Secondary pump power = 13W/gpm | Baseline RMR = expected value | none | No | Per Pump | Secondary pump power equals 13W per gpm | Baseline | Pass | Baseline CHW Secondary pump power is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:power pumps:design_flow |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary 1300 100 | One Story Template |  | IP
G3 | 11 | b | G3-11b | Secondary pump power = 13W/gpm | Baseline RMR = expected value | none | No | Per Pump | Secondary pump power does not equal 13W per gpm | Baseline | Fail | Baseline CHW Secondary pump power should be 13W per gpm | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:secondary_pump_name pumps:name pumps:type pumps:power pumps:design_flow |  |  | CHW_Loop_1 CHW SCHW_Pump_1 SCHW_Pump_1 secondary 1500 100 | One Story Template |  | IP
G3 | 12 | a | G3-12a | Purchased CHW Loop temp reset = none | Baseline RMR = expected value | none | No | Per Loop | Purchasaed CHW Loop temperature reset equals "none" | Baseline | Pass | Baseline Purchasaed CHW Loop temperature reset is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type |  |  | CHW_Loop_1 purchased_CHW none | One Story Template
G3 | 12 | b | G3-12b | Purchased CHW Loop temp reset = none | Baseline RMR = expected value | none | No | Per Loop | Purchasaed CHW Loop temperature reset does not equal "none" | Baseline | Fail | Baseline Purchasaed CHW Loop temperature reset should equal "none" | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:temperature_reset_type |  |  | CHW_Loop_1 purchased_CHW load reset | One Story Template
G3 | 13 | a | G3-13a | Purchased CHW loop has a distribution pump (T/F) | Baseline RMR = expected value | none | No | Per Loop | Purchased CHW Loop has a distribution pump | Baseline | Pass | Baseline Purchased CHW Loop has a distribution pump | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution | One Story Template
G3 | 13 | b | G3-13b | Purchased CHW loop has a distribution pump (T/F) | Baseline RMR = expected value | none | No | Per Loop | Purchased CHW Loop does not have a distribution pump | Baseline | Fail | Baseline Purchased CHW Loop does not have a distribution pump | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 secondary | One Story Template
G3 | 14 | a | G3-14a | Distribution pump speed control is a VFD | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution Pump speed control equals VFD | Baseline | Pass | Baseline Distribution Pump speed control is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:speed_control |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution VFD | One Story Template
G3 | 14 | b | G3-14b | Distribution pump speed control is a VFD | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution pumps peed control does not equal VFD | Baseline | Fail | Baseline Distribution Pump speed control should be VFD | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:speed_control |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution none | One Story Template
G3 | 15 | a | G3-15a | Distribution pump minimum flow setpoint = 25% | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution pump minimum speed control equals 25% | Baseline | Pass | Baseline Distribution pump minimum speed control is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:minimum_flow_fraction |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution 0.25 | One Story Template
G3 | 15 | b | G3-15b | Distribution pump minimum flow setpoint = 25% | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution pump minimum speed control does not equal 25% | Baseline | Pass | Baseline Distribution pump minimum speed control should be 25% | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:minimum_flow_fraction |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution 0.40 | One Story Template
G3 | 16 | a | G3-16a | Distribution pump power is 16W/gpm | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution pump power equals 16 W per gpm | Baseline | Pass | Baseline Distribution pump power is correct | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:power pumps:design_flow |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution 1600 100 | One Story Template |  | IP
G3 | 16 | b | G3-16b | Distribution pump power is 16W/gpm | Baseline RMR = expected value | Rule 13 is true | No | Per Pump | Distribution pump power does not equal 16W per gpm | Baseline | Pass | Baseline Distribution pump power should be 16W per gpm | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:distribution_pump_name pumps:name pumps:type pumps:power pumps:design_flow |  |  | CHW_Loop_1 purchased_CHW Pur_CHW_Pump_1 Pur_CHW_Pump_1 distribution 1800 100 | One Story Template |  | IP
G3 | 17 | a | G3-17a | Heat Rejection loop has a single heat rejection device attached? (T/F) | Baseline RMR = expected value | none | Yes | Per HR Device | Heat rejection loop has a single heat rejection device attached | Baseline | Pass | Baseline Heat rejection loop has a single heat rejection device attached | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:heat_rejection_name(1) hydronic_loops:heat_rejection_name(2) |  |  | HR_Loop_1 heat_rejection Cooling_tower_1 null | One Story Template
G3 | 17 | b | G3-17b | Heat Rejection loop has a single heat rejection device attached? (T/F) | Baseline RMR = expected value | none | Yes | Per HR Device | Heat rejection device has no heat rejection device attached | Baseline | Fail | Baseline heat rejection loop requires one heat rejection device be included. | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:heat_rejection_name(1) hydronic_loops:heat_rejection_name(2) |  |  | HR_Loop_1 heat_rejection null null | One Story Template
G3 | 17 | c | G3-17c | Heat Rejection loop has a single heat rejection device attached? (T/F) | Baseline RMR = expected value | none | Yes | Per HR Device | Heat rejection loop has more than one device attached | Baseline | Pass | Baseline heat rejection loop has more than one heat rejection device attached, only one is allowed. | hydronic_loops:loop_name hydronic_loops:type hydronic_loops:heat_rejection_name(1) hydronic_loops:heat_rejection_name(2) |  |  | HR_Loop_1 heat_rejection Cooling_tower_1 Cooling_tower_2 | One Story Template
G3 | 18 | a | G3-18a | Heat Rejection device type = axial fan | Baseline RMR = expected value | Rule 17 is true | Yes | Per HR Device | Heat rejection Type equals axial fan | Baseline | Pass | Baseline heat rejection type is correct | heat_rejection:name heat_rejection:type |  |  | Cooling_tower_1 axial_fan
G3 | 18 | b | G3-18b | Heat Rejection device type = axial fan | Baseline RMR = expected value | Rule 17 is true | Yes | Per HR Device | Heat rejection type does not equal axial fan | Baseline | Fail | Baseline heat rejection type should be axial fan | heat_rejection:name heat_rejection:type |  |  | Cooling_tower_1 dry_cooler
G3 | 19 | a | G3-19a | Heat rejection Device Range = 10 degrees | Baseline RMR = expected value | Rule 17 is true | No | Per HR Device | Heat rejection device range equals 10 | Baseline | Pass | Baseline heat rejection device range is correct | heat_rejection:name heat_rejection:range |  |  | Cooling_tower_1 5.6 |  |  | SI
G3 | 19 | b | G3-19b | Heat rejection Device Range = 10 degrees | Baseline RMR = expected value | Rule 17 is true | No | Per HR Device | Heat rejection device range does not equal 10 | Baseline | Fail | Baseline heat rejection device range should equal 10 | heat_rejection:name heat_rejection:range |  |  | Cooling_tower_1 4.5 |  |  | SI
G3 | 20 | a | G3-20a | Design Wet Bulb is 12.8C<=WB<=32.2C? (55F->90F) | Baseline RMR = expected value | Rule 17 is true | Yes | Per Project | Project location 0.4% MCWB is greater than or equal to 12.8C and less than or equal to 32.2C | Baseline | Pass | Project location 0.4% MCWB is greater than or equal to 12.8C and less than or equal to 32.2C | heat_rejection:name heat_rejection:design_wetbulb_temperature |  |  | Cooling_tower_1 23.9 |  |  | SI
G3 | 20 | b | G3-20b | Design Wet Bulb is 12.8C<=WB<=32.2C? (55F->90F) | Baseline RMR = expected value | Rule 17 is true | Yes | Per Project | Project location 0.4% MCWB is less than 12.8C | Baseline | Fail | Project location 0.4% MCWB is less than 12.8C, manually check Heat rejection device approach is appropriate for climate. | heat_rejection:name heat_rejection:design_wetbulb_temperature |  |  | Cooling_tower_1 11.1 |  |  | SI
G3 | 20 | c | G3-20c | Design Wet Bulb is 12.8C<=WB<=32.2C? (55F->90F) | Baseline RMR = expected value | Rule 17 is true | Yes | Per Project | Project location 0.4% MCWB is greater than 32.2C | Baseline | Fail | Project location 0.4% MCWB is greater than 32.2C, manually check Heat rejection device approach is appropriate for climate. | heat_rejection:name heat_rejection:design_wetbulb_temperature |  |  | Cooling_tower_1 33.3 |  |  | SI
G3 | 21 | a | G3-21a | Heat Rejection Device Approach calaculated correctly (T/F) | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection Device Approach is calculated correctly? | Baseline | Pass | Baseline heat rejection device approach is calculated correctly | heat_rejection:name heat_rejection:design_wetbulb_temperature heat_rejection:approach |  |  | Cooling_tower_1 23.9 5.6 |  | Uses formula to calculate approach based on 0.4%MCWBT | SI
G3 | 21 | b | G3-21b | Heat Rejection Device Approach calaculated correctly (T/F) | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection Device Approach is not calculated correctly? | Baseline | Fail | Baseline heat rejection device approach is not calculated correctly, correct value should be <RCT calculated value> | heat_rejection:name heat_rejection:design_wetbulb_temperature heat_rejection:approach |  |  | Cooling_tower_1 23.9 4.3 |  |  | SI
G3 | 22 | a | G3-22a | Heat Rejection Design Supply Temperature is correct | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat Rejection Supply Temperature is calcualted correctly? | Baseline | Pass | Baseline heat Rejection Supply Temperature is calcualted correctly | heat_rejection:name heat_rejection:design_wetbulb_temperature heat_rejection:design_supply_temperature |  |  | Cooling_tower_1 23.9 29.5 |  | Supply temp = 0.4%MCWBT+Approach | SI
G3 | 22 | b | G3-22b | Heat Rejection Design Supply Temperature is correct | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat Rejection Supply Temperature is not calcualted correctly? | Baseline | Fail | Baseline heat Rejection Supply Temperature is not calcualted correctly, correct value should be <RCT value> | heat_rejection:name heat_rejection:design_wetbulb_temperature heat_rejection:design_supply_temperature |  |  | Cooling_tower_1 23.9 28.3 |  |  | SI
G3 | 23 | a | G3-23a | Heat Rejection fan power = 3.47 L/s-kW (38.2 gpm/hp) | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection fan power equals 38 gpm per hp? | Baseline | Pass | Baseline heat rejection fan power is correct | heat_rejection:name heat_rejection:fan_power heat_rejection:design_water_flowrate |  |  | Cooling_tower_1 10 34.7 |  |  | SI
G3 | 23 | b | G3-23b | Heat Rejection fan power = 3.47 L/s-kW (38.2 gpm/hp) | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection fan power does not equal 38 gpm per hp? | Baseline | Fail | Baseline heat rejection fan power should equal 38 gpm per hp | heat_rejection:name heat_rejection:fan_power heat_rejection:design_water_flowrate |  |  | Cooling_tower_1 10 34.7 |  |  | SI
G3 | 24 | a | G3-24a | Heat Rejection fan speed control = VFD? | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection fan speed control equals VFD | Baseline | Pass | Baseline heat rejection fan speed control is correct | heat_rejection:name heat_rejection:fan_speed_control |  |  | Cooling_tower_1 VFD
G3 | 24 | b | G3-24b | Heat Rejection fan speed control = VFD? | Baseline RMR = expected value | Rule 36 is true | No | Per HR Device | Heat rejection fan speed control does not equal VFD | Baseline | Fail | Baseline heat rejection fan speed control should equal VFD | heat_rejection:name heat_rejection:fan_speed_control |  |  | Cooling_tower_1 two-speed
G3 | 25 | a | G3-25a | Heat Rejection Loop temperature reset = Load Reset | Baseline RMR = expected value | none | No | Per HR Device | Heat rejection loop temperature reset equals "load reset" | Baseline | Pass | Baseline heat rejection loop temperature reset type is correct | heat_rejection:name heat_rejection:fan_speed_control |  |  | Cooling_tower_1 VFD
G3 | 25 | b | G3-25b | Heat Rejection Loop temperature reset = Load Reset | Baseline RMR = expected value | none | No | Per HR Device | Heat rejection loop temperature reset equals "load reset" | Baseline | Pass | Baseline heat rejection loop temperature reset type is correct | heat_rejection:name heat_rejection:fan_speed_control |  |  | Cooling_tower_1 2-speed
G3 | 26 | a | G3-26a | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR = expected value | Rule 23 is true | Yes | Per Loop | Heat rejection loop minimum reset temperatrue equals Table G3.1.3.11 | Baseline | Pass | Baseline heat rejection loop minimum reset temperatrue is correct | heat_rejection:name heat_rejection:minimum_reset_temperature building:ASHRAE_climate_zone |  |  | Cooling_tower_1 18.3 5C
G3 | 26 | b | G3-26b | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR = expected value | Rule 23 is true | Yes | Per Loop | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Baseline | Fail | Baseline heat rejection loop minimum reset temperatrue is correct | heat_rejection:name heat_rejection:minimum_reset_temperature building:ASHRAE_climate_zone |  |  | Cooling_tower_1 21.1 3C
G3 | 26 | c | G3-26c | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR = expected value | Rule 23 is true | Yes | Per Loop | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Baseline | Fail | Baseline heat rejection loop minimum reset temperatrue is correct | heat_rejection:name heat_rejection:minimum_reset_temperature building:ASHRAE_climate_zone |  |  | Cooling_tower_1 23.9 4A
G3 | 26 | d | G3-26d | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR = expected value | Rule 23 is true | Yes | Per Loop | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Baseline | Fail | Baseline heat rejection loop minimum reset temperatrue is correct | heat_rejection:name heat_rejection:minimum_reset_temperature building:ASHRAE_climate_zone |  |  | Cooling_tower_1 26.7 1A
G3 | 26 | e | G3-26e | Miinimum condenser water reset temp is per Table G3.1.3.11? | Baseline RMR = expected value | Rule 23 is true | Yes | Per Loop | Heat rejection loop minimum reset temperatrue does not equal Table G3.1.3.11 | Baseline | Fail | Baseline heat rejection loop minimum reset temperature is not correct, correct value should be <RCT correct value> | heat_rejection:name heat_rejection:minimum_reset_temperature building:ASHRAE_climate_zone |  |  | Cooling_tower_1 26.7 5C
G3 | 27 | a | G3-27a | Chiller Type is correct per Table G3.1.3.7? | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller type is correct per Table G3.1.3.7? | Baseline | Pass | Baseline chiller type is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity chiller:name chiller:cooling_loop_name chiller:type |  |  | CHW_1 CHW 599 Chiller_1 CHW_1 water_cooled_screw
G3 | 27 | b | G3-27b | Chiller Type is correct per Table G3.1.3.7? | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller type is correct per Table G3.1.3.7? | Baseline | Pass | Baseline chiller type is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity chiller:name chiller:cooling_loop_name chiller:type |  |  | CHW_1 CHW 600 Chiller_1 CHW_1 water_cooled_centrifugal
G3 | 27 | c | G3-27c | Chiller Type is correct per Table G3.1.3.7? | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller type is not correct per Table G3.1.3.7? | Baseline | Fail | Baseline chiller type is not correct, correct type should be screw chiller | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity chiller:name chiller:cooling_loop_name chiller:type |  |  | CHW_1 CHW 550 Chiller_1 CHW_1 water_cooled_centrifugal
G3 | 27 | d | G3-27d | Chiller Type is correct per Table G3.1.3.7? | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller type is not correct per Table G3.1.3.7? | Baseline | Fail | Baseline chiller type is not correct, correct type should be <RCT value> | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity chiller:name chiller:cooling_loop_name chiller:type |  |  | CHW_1 CHW 700 Chiller_1 CHW_1 water_cooled_screw
G3 | 28 | a | G3-28a | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is correct based on type and capacity | Baseline | Pass | Baseline chiller efficiency is correct | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_screw 149 0.790
G3 | 28 | b | G3-28b | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is correct based on type and capacity | Baseline | Pass | Baseline chiller efficiency is correct | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_screw 299 0.718
G3 | 28 | c | G3-28c | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is correct based on type and capacity | Baseline | Pass | Baseline chiller efficiency is correct | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_centrifugal 300 0.576
G3 | 28 | d | G3-28d | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is not correct based on type and capacity | Baseline | Fail | Baseline chiller efficiency is not correct, correct value should be 0.576 | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_centrifugal 300 0.718
G3 | 28 | e | G3-28e | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is not correct based on type and capacity | Baseline | Fail | Baseline chiller efficiency is not correct, correct value should be <RCT value> | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_screw 299 0.576
G3 | 28 | f | G3-28f | Chiller efficiency is correct per Table G3.5.3 | Baseline RMR = expected value | none | Yes | Per Chiller | Chiller efficiency is not correct based on type and capacity | Baseline | Pass | Baseline chiller efficiency is not correct, correct value should be <RCT value> | hydronic_loops:name hydronic_loops:type chiller:name chiller:cooling_loop_name chiller:type chiller:design_capacity chiller:efficiency |  |  | CHW_1 CHW Chiller_1 CHW_1 water_cooled_screw 149 .676
G3 | 29 | a | G3-29a | Chiller has an associated primary pump? | Baseline RMR = expected value | none | No | Per Chiller | Chiller has an associated primary pump | Baseline | Pass | Baseline chiller has an associated primary pump | chiller:name chiller:primary_pumps_name pumps:name pumps:type |  |  | Chiller_1 PCHW_Pump_1 PCHW_Pump_1 primary_CHW
G3 | 29 | b | G3-29b | Chiller has an associated primary pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller does not have an associated primary pump | Baseline | Fail | Baseline chiller does not have an associated primary pump | chiller:name chiller:primary_pumps_name pumps:name pumps:type |  |  | Chiller_1 PCHW_Pump_1 null null
G3 | 29 | c | G3-29c | Chiller has an associated primary pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller does not have an associated primary pump | Baseline | Fail | Baseline chiller does not have an associated primary pump | chiller:name chiller:primary_pumps_name pumps:name pumps:type |  |  | Chiller_1 PCHW_Pump_1 PCHW_Pump_1 secondary_CHW
G3 | 30 | a | G3-30a | Primary pump sepeed control = constant | Baseline RMR = expected value | rule 27 is true | No | Per Chiller | primary pump speed control equals constant | Baseline | Pass | Baseline primary pump speed control is correct | pumps:name pumps:type pumps:speed_control |  |  | PCHW_Pump_1 primary_CHW constant
G3 | 30 | b | G3-30b | Primary pump sepeed control = constant | Baseline RMR = expected value | rule 27 is true | No | Per Chiller | pimary pump speed control does not equal constant | Baseline | Fail | Baseline primary pump speed control should be constant | pumps:name pumps:type pumps:speed_control |  |  | PCHW_Pump_1 primary_CHW VFD
G3 | 31 | a | G3-31a | Primary pump power = 9W/gpm | Baseline RMR = expected value | Rule 27 is true and Loop doesn't serve System 11 | No | Per Chiller | primary pump power equals 9W per gpm | Baseline | Pass | Baseline primary pump power is correct | pumps:name pumps:type pumps:power pumps:design_flow |  |  | PCHW_Pump_1 primary_CHW 900 100
G3 | 31 | b | G3-31b | Primary pump power = 9W/gpm | Baseline RMR = expected value | Rule 27 is true and Loop doesn't serve System 11 | No | Per Chiller | Primary pump power does not equal 9W per gpm | Baseline | Fail | Baseline primary pump power should be 9W per gpm | pumps:name pumps:type pumps:power pumps:design_flow |  |  | PCHW_Pump_1 primary_CHW 1000 100
G3 | 32 | a | G3-32a | Primary pump power = 12W/gpm | Baseline RMR = expected value | Rule 27 is true and Loop serves system 11 | No | Per Chiller | Primary pump power equals 12W per gpm when loop uses system 11. | Baseline | Pass | Baseline primary pump power is correct | pumps:name pumps:type pumps:power pumps:design_flow hydronic_loops:name hydronic_loops:serves_ystem_type_11 |  |  | PCHW_Pump_1 primary_CHW 1200 100 CHW_1 True
G3 | 32 | b | G3-32b | Primary pump power = 12W/gpm | Baseline RMR = expected value | Rule 27 is true and Loop serves system 11 | No | Per Chiller | Primary pump power does not equal 12W per gpm when loop uses system 11. | Baseline | Fail | Baseline primary pump power should be 12W per gpm when loop serves baseline system type 11. | pumps:name pumps:type pumps:power pumps:design_flow hydronic_loops:name hydronic_loops:serves_ystem_type_11 |  |  | PCHW_Pump_1 primary_CHW 1400 100 CHW_1 True
G3 | 33 | a | G3-33a | Chiller has an associated condenser pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller has an associated condenser pump | Baseline | Pass | Baseline Baseline chiller has an associated condenser pump | chiller:name chiller:condenser_pumps_name pumps:name pumps:type |  |  | Chiller_1 CW_Pump_1 CW_Pump_1 condenser
G3 | 33 | b | G3-33b | Chiller has an associated condenser pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller does not have an associated condenser pump of the correct type | Baseline | Fail | Baseline chiller does not have an associated condenser pump | chiller:name chiller:condenser_pumps_name pumps:name pumps:type |  |  | Chiller_1 CW_Pump_1 CW_Pump_1 primary
G3 | 33 | c | G3-33c | Chiller has an associated condenser pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller does not have an associated condenser pump | Baseline | Fail | Baseline chiller does not have an associated condenser pump | chiller:name chiller:condenser_pumps_name pumps:name pumps:type |  |  | Chiller_1 null CW_Pump_1 condenser
G3 | 33 | d | G3-33d | Chiller has an associated condenser pump? | Baseline RMR = expected value | none | No | Per Chiller | chiller associated condenser pump name does not exist as a pump object | Baseline | Fail | Baseline chiller does not have an associated condenser pump | chiller:name chiller:condenser_pumps_name pumps:name pumps:type |  |  | Chiller_1 CW_Pump_1 null null
G3 | 34 | a | G3-34a | Condenser pump speed control = constant | Baseline RMR = expected value | Rule 31 is true | No | Per Chiller | condenser pump speed control equals constant | Baseline | Pass | Baseline condenser pump speed control is correct | pumps:name pumps:type pumps:speed_control |  |  | CW_Pump_1 condenser constant
G3 | 34 | b | G3-34b | Condenser pump speed control = constant | Baseline RMR = expected value | Rule 31 is true | No | Per Chiller | condenser pump speed control does not equal constant | Baseline | Fail | Baseline condenser pump speed control should be constant | pumps:name pumps:type pumps:speed_control |  |  | CW_Pump_1 condenser VFD
G3 | 35 | a | G3-35a | Condenser pump power is 19W/gpm | Baseline RMR = expected value | Rule 31 is true and loop does not serve system type 11 | No | Per Chiller | condenser pum power equals 19W per gpm | Baseline | Pass | Baseline condenser pum power is correct | pumps:name pumps:type pumps:power pumps:design_flow |  |  | CW_Pump_1 condenser 1900 100
G3 | 35 | b | G3-35b | Condenser pump power is 19W/gpm | Baseline RMR = expected value | Rule 31 is true and loop does not serve system type 11 | No | Per Chiller | condenser pump power does not equal 19W per gpm | Baseline | Fail | Baseline condenser pump power should be 19W per gpm | pumps:name pumps:type pumps:power pumps:design_flow |  |  | CW_Pump_1 condenser 2200 100
G3 | 36 | a | G3-36a | Distribution pump power is 22W/gpm | Baseline RMR = expected value | Rule 31 is true and loop serves system type 11 | No | Per Pump | Distribution pump power equals 22 W per gpm | Baseline | Pass | Baseline distribution pump power is correct | pumps:name pumps:type pumps:power pumps:design_flow |  |  | Prch_CHW_Pump_1 distribution 2200 100
G3 | 36 | b | G3-36b | Distribution pump power is 22W/gpm | Baseline RMR = expected value | Rule 31 is true and loop serves system type 11 | No | Per Pump | Distribution pump power does not equal 22W per gpm | Baseline | Fail | Baseline distribution pump power should be 22W per gpm | pumps:name pumps:type pumps:power pumps:design_flow |  |  | Prch_CHW_Pump_1 distribution 2000 100
G3 | 37 | a | G3-37a | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW Loop has correct number of chillers based on load | Baseline | Pass | Baseline CHW Loop has correct number of chillers | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 300 Chiller_1 null null null
G3 | 37 | b | G3-37b | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW Loop has correct number of chillers based on load | Baseline | Pass | Baseline CHW Loop has correct number of chillers | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 600 Chiller_1 Chiller_2 null null
G3 | 37 | c | G3-37c | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW Loop has correct number of chillers based on load | Baseline | Pass | Baseline CHW Loop has correct number of chillers | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 600 Chiller_1 Chiller_2 null null
G3 | 37 | d | G3-37d | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW Loop has correct number of chillers based on load | Baseline | Pass | Baseline CHW Loop has correct number of chillers | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 2400 Chiller_1 Chiller_2 Chiller_3 null
G3 | 37 | e | G3-37e | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW Loop has correct number of chillers based on load | Baseline | Pass | Baseline CHW Loop has correct number of chillers | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 3200 Chiller_1 Chiller_2 Chiller_3 Chiller_4
G3 | 37 | f | G3-37f | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW loop does not have correct number of chillers based on load | Baseline | Fail | Baseline CHW loop does not have correct number of chillers, correct number should be two(2) | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 600 Chiller_1 null null null
G3 | 37 | g | G3-37g | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW loop does not have correct number of chillers based on load | Baseline | Fail | Baseline CHW loop does not have correct number of chillers, correct number should be three(3) | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 2000 Chiller_1 Chiller_2 Chiller_3 Chiller_4
G3 | 37 | h | G3-37h | CHW Loop has correct number of chillers based on Table G3.1.3.7 | Baseline RMR = expected value | none | Yes | Per Loop | CHW loop does not have correct number of chillers based on load | Baseline | Fail | Baseline CHW loop does not have correct number of chillers, correct number should be two(2) | hydronic_loops:name hydronic_loops:type hydronic_loops:peak_cooling_capacity hydronic_loops:chiller_name(1) hydronic_loops:chiller_name(2) hydronic_loops:chiller_name(3) hydronic_loops:chiller_name(4) |  |  | CHW_1 CHW 900 Chiller_1 null null null
G3 | 38 | a | G3-38a | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power equals 22 W per gpm | #N/A | Pass | Baseline chiller capacity is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 300 Chiller_1 CHW_1 300
G3 | 38 | b | G3-38b | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power equals 22 W per gpm | #N/A | Pass | Baseline chiller capacity is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 580 Chiller_1 CHW_1 290
G3 | 38 | c | G3-38c | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power equals 22 W per gpm | #N/A | Pass | Baseline chiller capacity is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 1500 Chiller_1 CHW_1 750
G3 | 38 | d | G3-38d | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power equals 22 W per gpm | #N/A | Pass | Baseline chiller capacity is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 2100 Chiller_1 CHW_1 700
G3 | 38 | e | G3-38e | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power equals 22 W per gpm | #N/A | Pass | Baseline chiller capacity is correct | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 2400 Chiller_1 CHW_1 800
G3 | 38 | f | G3-38f | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power does not equal 22W per gpm | #N/A | Fail | Baseline chiller capacity is not correct, the correct capacity should be 290 | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 580 Chiller_1 CHW_1 300
G3 | 38 | g | G3-38g | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power does not equal 22W per gpm | #N/A | Fail | Baseline chiller capacity is not correct, the correct capacity should be 700 | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 2100 Chiller_1 CHW_1 800
G3 | 38 | h | G3-38h | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power does not equal 22W per gpm | #N/A | Fail | Baseline chiller capacity is not correct, the correct capacity should be 800 | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 1600 Chiller_1 CHW_1 900
G3 | 38 | i | G3-38i | Chiller capacity is correct | Baseline RMR = expected value | Rule 37 is true | Yes | Per Chiller | Distribution pump power does not equal 22W per gpm | #N/A | Fail | Baseline chiller capacity is not correct, the correct capacity should be 150 | hydronic_loops:name hydronic_loops:type hydronic_loops:design_capacity chiller:name chiller:cooling_loop_name chiller:design_capacity |  |  | CHW_1 CHW 150 Chiller_1 CHW_1 300
Note on S30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Sheet1
Rule ID | Test ID | Test Scope | Test Description | Expected Test Outcome | Test Outcome Text | Attribute Names (variables needed for test) | User RMR Value(s) | Proposed RMR Value(s) | Baseline RMR Value(s)
DISTRIBUTION TRANSFORMERS
1 | 1-1 | Loop | Loop supply temperature = 44F | TRUE | CHW Loop 1 has the correct CHWST in the Base RMR | Loop_Name Loop_CHWST |  |  | CHW_Loop_1 44