## Rules
App G Section ID | Rule ID | Rule Description | Applicable RMR | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Note | Complexity | Importance | Triggers
11 | 1 | Proposed RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Proposed | Proposed RMR = User RMR | none | No
11 | 2 | Number of service water heating systems in Baseline RMR = User RMR | Baseline | Baseline RMR = User RMR | SWH Loops in User RMR = 0 | No
11 | 3 | Number of service water heating systems in Proposed RMR = User RMR | Proposed | Proposed RMR = User RMR | none | No
11 | 4 | All SWH loops in User RMR have same design paramters | User | User RMR sameness | User RMR SWH Loops Count > 1 | No | Design paramters to test are entering loop temperature, supply water temperature setpoint and flow schedules
11 | 5 | SWH loop in User RMR is found in Proposed RMR | Proposed | Proposed RMR = User RMR | User RMR SWH Loops Count > 0 | No
11 | 6 | SWH Loop flow schedule in Proposed RMR is the same as the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 is true | No
11 | 7 | SWH Loop Design Flow in Proposed RMR is the same as the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 is true | No
11 | 8 | SWH Loop Design Supply Water Temperature setpoint in Proposed RMR is the same as the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 is true | No
11 | 9 | SWH Loop entering water temperature type in Proposed RMR is the same as the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 is true | No
11 | 10 | SWH Heater name in User RMR is also in the Proposed RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 is true | No
11 | 11 | SWH Heater capacity in Proposed RMR is equal to the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No
11 | 12 | SWH Heater efficiency in Proposed RMR is equal to the User RMR | Proposed | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No
11 | 13 | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | No
11 | 14 | SWH Loop flow schedule in Baseline RMR is the same as the User RMR | Baseline | Baseline RMR = User RMR | Rule 11-4 is True | No
11 | 15 | SWH Loop Design Supply Water Temperature setpoint in Baseline RMR is the same as the User RMR | Baseline | Baseline RMR = User RMR | Rule 11-4 is True | No
11 | 16 | SWH Loop entering water temperature type in Baseline RMR is the same as the User RMR | Baseline | Baseline RMR = User RMR | Rule 11-4 is True | No
11 | 17 | SWH Heater Fuel Type in Baseline RMR = expected value | Baseline | Baseline RMR = expected value | Rule 11-4 is true | Yes
11 | 18 | SWH Heater Efficiency in Baseline RMR = expected value | Baseline | Baseline RMR = expected value | Rule 11-4 is True | Yes
11 | 19 | Baseline RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Baseline | Baseline RMR = User RMR | none | No
Note on H11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Schema Data Elements
Data_Group | Attribute Names (variables needed for test) | Std 229 Schema Name | Description | Units | Type | Enumerations
service_water_heating | loop_name |  | Service Water Heating Loop name | none | Text
service_water_heating | area_type |  | Service Water Heating Loop Area Type | none | Value List | Area types in Table G3.1.1-2
service_water_heating | design_flow |  | Design Flowrate of SWH loop | gpm or L/s | Number
service_water_heating | supply_temperature |  | Design supply temperature setpoint of SWH loop | degrees C | Number
service_water_heating | flow_schedule |  | SWH Loop flow schedule name | none | Text
service_water_heating | annual_entering_water_temp |  | Annual service main or annual ground temperature used for SWH calculations entering water temperature | degrees C | Number
service_water_heating | monthly_entering_water_temp |  | Monrthly service main or ground temperatures used for SWH entering water temperature | degrees C | Array | Arrayed variable with 12 values for monthly entering water temperature
service_water_heating | entering_water_temperature_type |  | Method of determining SWH entering water temperature | none | Value List | Annual_Main, Monthly_Main, Annual_Ground, Monthly_Ground
service_water_heating | heater_name |  | SWH heater name | none | text
service_water_heating | heater_fuel_type |  | SWH heater fuel type | none | enumeration | electric, gas
service_water_heating | heater_efficiency |  | SWH heater efficiency | none | value
service_water_heating | building_area_type |  | SWH building area type from App G | none | enumeration | Table G3.1.1-2
service_water_heating | annual_enduse_electricity |  | Annual electricity energy end_use for SWH loops | kWh | Number
service_water_heating | annual_enduse_fossilfuel |  | Annual fossil fuel energy end_use for SWH loops | MMBTU | Number
Note on D19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)

## Test Case Descriptions
App G Section ID | Rule ID | Test ID | Unique ID | Rule Description | Rule Assertion | Rule Dependency (Triggers) | Data lookup required | Test Scope | Test Description | RMR Tested | Expected Test Outcome | Test Outcome Text | Attribute Names (variables needed for test) | User RMR Value(s) | Proposed RMR Value(s) | Baseline RMR Value(s) | Test Case RMR Template | Note
DISTRIBUTION TRANSFORMERS
11 | 1 | a | 11-1a | Proposed RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Proposed RMR = User RMR | none | No | Project | service_water_heating energy in Proposed RMR = User RMR | Proposed | Pass | Annual service_water_heating energy is the same in both the Proposed and User RMR files | service_water_heating:annual_enduse_electricity service_water_heating:annual_enduse_fossilfuel | 10000 0 | 10000 0 | 10000 0 | One Story Template
11 | 1 | b | 11-1b | Proposed RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Proposed RMR = User RMR | none | No | Project | service_water_heating energy in Proposed RMR does not equal User RMR | Proposed | Fail | Annual service_water_heating energy is not the same in the Proposed and User RMR files | service_water_heating:annual_enduse_electricity service_water_heating:annual_enduse_fossilfuel | 10000 0 | 15000 0 | 15000 0 | One Story Template
11 | 2 | a | 11-2a | Number of service water heating systems in Baseline RMR = User RMR | Baseline RMR = User RMR | SWH Loops in User RMR = 0 | No | Project | service_water_heating count in Baseline RMR = User RMR, User RMR = 0 | Baseline | Pass | Service Water Heating systems are not modeled in the User RMR or the Baseline RMR | service_water_heating:loop_name | null |  | null | One Story Template
11 | 2 | b | 11-2b | Number of service water heating systems in Baseline RMR = User RMR | Baseline RMR = User RMR | SWH Loops in User RMR = 0 | No | Project | service_water_heating count in Baseline RMR > 0 | Baseline | Fail | Service Water heating systems are not modeled in the User RMR, but are included in the Baseline RMR. | service_water_heating:loop_name | null |  | SWH_loop1 | One Story Template
11 | 3 | a | 11-3a | Number of service water heating systems in Proposed RMR = User RMR | Proposed RMR = User RMR | none | No | Project | service_water_heating count in User RMR = 0, Proposed RMR count = 0 | Proposed | Pass | No service_water_heating loops are included in the User RMR or the Proposed RMR | service_water_heating:loop_name | null | null |  | One Story Template
11 | 3 | b | 11-3b | Number of service water heating systems in Proposed RMR = User RMR | Proposed RMR = User RMR | none | No | Project | service_water_heating count in User RMR = 0, Proposed RMR count >0 | Proposed | Fail | Service water heating loops are not modeled in the User RMR but are included in the Propsoed RMR, this is unexpected. | service_water_heating:loop_name | null | SWH_Loop |  | One Story Template
11 | 3 | c | 11-3c | Number of service water heating systems in Proposed RMR = User RMR | Proposed RMR = User RMR | none | No | Project | service_water_heating count in User RMR > 0, Proposed RMR count = User RMR count | Proposed | Pass | The number of reported service_water_heating in the User RMR is the same as in the Proposed RMR | service_water_heating:loop_name service_water_heating:loop_name | SHW_Loop1 SHW_Loop2 | SHW_Loop1 SHW_Loop2 |  | One Story Template
11 | 3 | d | 11-3d | Number of service water heating systems in Proposed RMR = User RMR | Proposed RMR = User RMR | none | No | Project | service_water_heating count in User RMR > 0, Proposed RMR count does not equal User RMR count | Proposed | Fail | The number of reported service_water_heating loops reported in the User RMR does not match the Proposed RMR | service_water_heating:loop_name service_water_heating:loop_name | SHW_Loop1 SHW_Loop2 | SHW_Loop1 null |  | One Story Template
11 | 4 | a | 11-4a | All SWH loops in User RMR have same design paramters | User RMR sameness | User RMR SWH Loops Count > 1 | No | Per SWH Loop | service_water_heating loop design parameters are all the same | User | Pass | The service_water_heating loop design parameters are all the same therefore Baseline SWH loop design paramaters can be verified. | service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type | SWH_Loop1 SWH_Schedule 130 Annual SWH_Loop2 SWH_Schedule 130 Annual |  |  | One Story Template
11 | 4 | b | 11-4b | All SWH loops in User RMR have same design paramters | User RMR sameness | User RMR SWH Loops Count > 1 | No | Per SWH Loop | service_water_heating loop design parameters are not all the same | User | Fail | The service_water_heating loop design parameters are not all the same therefore Baseline SWH loop design paramaters cannot be verified by the RCT. | service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type | SWH_Loop1 SWH_Schedule 130 Annual SWH_Loop2 SWH_Schedule 125 Annual |  |  | One Story Template
11 | 4 | c | 11-4c | All SWH loops in User RMR have same design paramters | User RMR sameness | User RMR SWH Loops Count > 1 | No | Per SWH Loop | service_water_heating loop design parameters are not all the same | User | Fail | The service_water_heating loop design parameters are not all the same therefore Baseline SWH loop design paramaters cannot be verified by the RCT. | service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type | SWH_Loop1 SWH_Schedule 130 Annual SWH_Loop2 SWH_Sch_2 130 Annual |  |  | One Story Template
11 | 4 | d | 11-4d | All SWH loops in User RMR have same design paramters | User RMR sameness | User RMR SWH Loops Count > 1 | No | Per SWH Loop | service_water_heating loop design parameters are not all the same | User | Fail | The service_water_heating loop design parameters are not all the same therefore Baseline SWH loop design paramaters cannot be verified by the RCT. | service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type service_water_heating:loop_name service_water_heating:flow_schedule service_water_heating:supply_temperature service_water_heating:entering_water_temperature_type | SWH_Loop1 SWH_Schedule 130 Annual SWH_Loop2 SWH_Schedule 130 Monthly |  |  | One Story Template
11 | 5 | a | 11-5a | SWH loop in User RMR is found in Proposed RMR | Proposed RMR = User RMR | User RMR SWH Loops Count > 0 | No | Per SWH Loop | User RMR service_water_heating name is in the Proposed RMR | Proposed | Pass | The SWH_Loop <service_water_heating loop_name> in the User RMR has a corresponding SWH System in the Proposed RMR | service_water_heating:loop_name service_water_heating:loop_name | SWH_Loop1 SWH_Loop2 | SWH_Loop1 SWH_Loop2 |  | One Story Template
11 | 5 | b | 11-5b | SWH loop in User RMR is found in Proposed RMR | Proposed RMR = User RMR | User RMR SWH Loops Count > 0 | No | Per SWH Loop | User RMR service_water_heating name is not in the Proposed RMR | Proposed | Fail | The SWH_Loop <service_water_heating loop_name> in the User RMR does not have a corresponding service_water_heating system in the Proposed RMR | service_water_heating:loop_name service_water_heating:loop_name | SWH_Loop1 SWH_Loop2 | SWH_Loop1 SWH_Loop3 |  | One Story Template
11 | 6 | a | 11-6a | SWH Loop flow schedule in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating flow_schedule is the same as in the Proposed RMR | Proposed | Pass | The flow schedule in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:flow_schedule | SWH_Loop1 SWH_Schedule | SWH_Loop1 SWH_Schedule |  | One Story Template
11 | 6 | b | 11-6b | SWH Loop flow schedule in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating flow_schedule is not the same as in the Proposed RMR | Proposed | Fail | The flow schedule in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is not the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:flow_schedule | SWH_Loop1 SWH_Schedule | SWH_Loop1 SWH_Sch2 |  | One Story Template
11 | 7 | a | 11-7a | SWH Loop Design Flow in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating design_flow is the same as in the Proposed RMR | Proposed | Pass | The design flow in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:design_flow | SWH_Loop1 10 | SWH_Loop1 10 |  | One Story Template
11 | 7 | b | 11-7b | SWH Loop Design Flow in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating design_flow is the same as in the Proposed RMR | Proposed | Pass | The design flow in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:design_flow | SWH_Loop1 10 | SWH_Loop1 15 |  | One Story Template
11 | 8 | a | 11-8a | SWH Loop Design Supply Water Temperature setpoint in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating design supply temperature is the same as in the Proposed RMR | Proposed | Pass | The design supply temperature in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:supply_temperature | SWH_Loop1 130 | SWH_Loop1 130 |  | One Story Template
11 | 8 | b | 11-8b | SWH Loop Design Supply Water Temperature setpoint in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating design supply temperature is not the same as in the Proposed RMR | Proposed | Pass | The design supply temperature in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is not the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:supply_temperature | SWH_Loop1 130 | SWH_Loop1 125 |  | One Story Template
11 | 9 | a | 11-9a | SWH Loop entering water temperature type in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating entering water temperature type is the same as in the Proposed RMR | Proposed | Pass | The entering water temperature type in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:entering_water_temperature_type | SWH_Loop1 Annual | SWH_Loop1 Annual |  | One Story Template
11 | 9 | b | 11-9b | SWH Loop entering water temperature type in Proposed RMR is the same as the User RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SWH Loop | User RMR service_water_heating entering water temperature type is the same as in the Proposed RMR | Proposed | Pass | The entering water temperature type in SWH_Loop <service_water_heating loop_name> in the Proposed RMR is not the same as the corresponding SWH System in the User RMR | service_water_heating:loop_name service_water_heating:entering_water_temperature_type | SWH_Loop1 Annual | SWH_Loop1 Mnthly |  | One Story Template
11 | 10 | a | 11-10a | SWH Heater name in User RMR is also in the Proposed RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SHW Heater | SHW Heater name in the User RMR has a corresponding SHW Heater in the Propsoed RMR | Proposed | Pass | The SHW Heater <service_water_heating heater_name> in the User RMR has a corresponding SWH heater in the Proposed RMR | service_water_heating:heater_name | SWH_Heater1 | SWH_Heater1 |  | One Story Template
11 | 10 | b | 11-10b | SWH Heater name in User RMR is also in the Proposed RMR | Proposed RMR = User RMR | Rule 11-5 is true | No | Per SHW Heater | SHW Heater name in the User RMR has a corresponding SHW Heater in the Propsoed RMR | Proposed | Pass | The SHW Heater <service_water_heating heater_name> in the User RMR has a corresponding SWH heater in the Proposed RMR | service_water_heating:heater_name | SWH_Heater1 | SWH_Heater2 |  | One Story Template
11 | 11 | a | 11-11a | SWH Heater capacity in Proposed RMR is equal to the User RMR | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No | Per SWH Heater | Capacity of a SHW Heater in the Proposed RMR is the same as the corresponding SHW Heater in the Proposed RMR | Proposed | Pass | The capacity of SHW Heater <service_water_heating heater_name> in the Proposed RMR is the same as in the User RMR | service_water_heating:heater_name service_water_heating:heater_capacity | SWH_Heater1 100 | SWH_Heater1 100 |  | One Story Template
11 | 11 | b | 11-11b | SWH Heater capacity in Proposed RMR is equal to the User RMR | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No | Per SWH Heater | Capacity of a SHW Heater in the Proposed RMR is the same as the corresponding SHW Heater in the Proposed RMR | Proposed | Pass | The capacity of SHW Heater <service_water_heating heater_name> in the Proposed RMR is the same as in the User RMR | service_water_heating:heater_name service_water_heating:heater_capacity | SWH_Heater1 100 | SWH_Heater1 150 |  | One Story Template
11 | 12 | a | 11-12a | SWH Heater efficiency in Proposed RMR is equal to the User RMR | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No | Per SHW Heater | Efficiency of a SHW Heater in the Proposed RMR is the same as the corresponding SHW Heater in the Proposed RMR | Proposed | Pass | The efficiency of SHW Heater <service_water_heating heater_name> in the Proposed RMR is the same as in the User RMR | service_water_heating:heater_name service_water_heating:heater_efficiency | SWH_Heater1 90% | SWH_Heater1 90% |  | One Story Template
11 | 12 | b | 11-12b | SWH Heater efficiency in Proposed RMR is equal to the User RMR | Proposed RMR = User RMR | Rule 11-5 and Rule 11-10 are true | No | Per SHW Heater | Efficiency of a SHW Heater in the Proposed RMR is the same as the corresponding SHW Heater in the Proposed RMR | Proposed | Pass | The efficiency of SHW Heater <service_water_heating heater_name> in the Proposed RMR is the same as in the User RMR | service_water_heating:heater_name service_water_heating:heater_efficiency | SWH_Heater1 90% | SWH_Heater1 80% |  | One Story Template
11 | 13 | a | 11-13a | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | No | Per Project | Total flow of all loops in User RMR equals total flow of all loops in Baseline RMR | Baseline | Pass | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow | SHW_Loop1 90 |  | SHW_Loop1 90 | One Story Template
11 | 13 | b | 11-13b | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | No | Per Project | Total flow of all loops in User RMR is not equal to total flow of all loops in Baseline RMR | Baseline | Fail | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow | SHW_Loop1 90 |  | SHW_Loop1 80 | One Story Template
11 | 13 | c | 11-13c | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | no | Per Project | Total flow of all loops in User RMR equals total flow of all loops in Baseline RMR | Baseline | Pass | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow service_water_heating:name service_water_heating:design_flow | SHW_Loop1 90 null null |  | SHW_Loop1 45 SHW_Loop1 45 | One Story Template
11 | 13 | d | 11-13d | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | no | Per Project | Total flow of all loops in User RMR is not equal to total flow of all loops in Baseline RMR | Baseline | Fail | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow service_water_heating:name service_water_heating:design_flow | SHW_Loop1 90 null null |  | SHW_Loop1 45 SHW_Loop1 50 | One Story Template
11 | 13 | e | 11-13e | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | No | Per Project | Total flow of all loops in User RMR equals total flow of all loops in Baseline RMR | Baseline | Pass | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow service_water_heating:name service_water_heating:design_flow | SHW_Loop1 45 SHW_Loop1 50 |  | SHW_Loop1 90 null null | One Story Template
11 | 13 | f | 11-13f | Sum of Design Flows of User RMR SWH Loops equals Sum of Design Flows of Baseline RMR SWH Loops | Baseline RMR = User RMR | User RMR SWH Loop Count >0 | No | Per Project | Total flow of all loops in User RMR is not equal to total flow of all loops in Baseline RMR | Baseline | Fail | The total SHW design flow in the User RMR is equal to the total design flow in the Baseline RMR. | service_water_heating:name service_water_heating:design_flow service_water_heating:name service_water_heating:design_flow | SHW_Loop1 45 SHW_Loop1 50 |  | SHW_Loop1 90 null null | One Story Template
11 | 14 | a | 11-14a | SWH Loop flow schedule in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating flow_schedule is the same in each SWH loop in the Baseline RMR | Baseline | Pass | The flow schedule in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is the same as in the User RMR | service_water_heating:loop_name service_water_heating:flow_schedule | SWH_Loop1 SWH_Schedule |  | SWH_Loop1 SWH_Schedule | One Story Template
11 | 14 | b | 11-14b | SWH Loop flow schedule in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating flow_schedule is not the same as in the Baseline RMR | Baseline | Fail | The flow schedule in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is not the same as in the User RMR | service_water_heating:loop_name service_water_heating:flow_schedule | SWH_Loop1 SWH_Schedule |  | SWH_Loop1 SWH_Sch2 | One Story Template
11 | 15 | a | 11-15a | SWH Loop Design Supply Water Temperature setpoint in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating design supply temperature is the same as in the Baseline RMR | Baseline | Pass | The design supply temperature in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is the same as in the User RMR | service_water_heating:loop_name service_water_heating:supply_temperature | SWH_Loop1 130 |  | SWH_Loop1 130 | One Story Template | May require further interpretation of requirements. Does capacity ratio need to be the same if fluid-filled modeled? Also for Schema does data element require just capacity ratio or capacity and peak load?
11 | 15 | b | 11-15b | SWH Loop Design Supply Water Temperature setpoint in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating design supply temperature is not the same as in the Baseline RMR | Baseline | Pass | The design supply temperature in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is not the same as in the User RMR | service_water_heating:loop_name service_water_heating:supply_temperature | SWH_Loop1 130 |  | SWH_Loop1 125 | One Story Template
11 | 16 | a | 11-16a | SWH Loop entering water temperature type in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating entering water temperature type is the same as in the Baseline RMR | Baseline | Pass | The entering water temperature type in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is the same as in the User RMR | service_water_heating:loop_name service_water_heating:entering_water_temperature_type | SWH_Loop1 Annual |  | SWH_Loop1 Annual | One Story Template
11 | 16 | b | 11-16b | SWH Loop entering water temperature type in Baseline RMR is the same as the User RMR | Baseline RMR = User RMR | Rule 11-4 is True | No | Per SWH Loop | User RMR service_water_heating entering water temperature type is the same as in the Baseline RMR | Baseline | Pass | The entering water temperature type in SWH_Loop <service_water_heating loop_name> in the Baseline RMR is not the same as in the User RMR | service_water_heating:loop_name service_water_heating:entering_water_temperature_type | SWH_Loop1 Annual |  | SWH_Loop1 Mnthly | One Story Template
11 | 17 | a | 11-17a | SWH Heater Fuel Type in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is true | Yes | Per SHW Heater | Fuel Type of the SHW Heater in the Baseline RMR = expected value | Baseline | Pass | The fuel type of the SHW Heater <service_water_heating heater_name> in the Baseline RMR is correct | service_water_heating:heater_name service_water_heating:heater_fuel_type service_water_heating:building_area_type |  |  | SWH_Heater1 electric Library | One Story Template
11 | 17 | b | 11-17b | SWH Heater Fuel Type in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is true | Yes | Per SHW Heater | Fuel Type of the SHW Heater in the Baseline RMR does not equal the expected value | Baseline | Fail | The fuel type of the SHW Heater <service_water_heating heater_name> in the Baseline RMR is not correct | service_water_heating:heater_name service_water_heating:heater_fuel_type service_water_heating:building_area_type |  |  | SWH_Heater1 gas Library | One Story Template
11 | 17 | c | 11-17c | SWH Heater Fuel Type in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is true | Yes | Per SHW Heater | Fuel Type of the SHW Heater in the Baseline RMR = expected value | Baseline | Pass | The fuel type of the SHW Heater <service_water_heating heater_name> in the Baseline RMR is correct | service_water_heating:heater_name service_water_heating:heater_fuel_type service_water_heating:building_area_type |  |  | SWH_Heater1 gas Dormitory | One Story Template
11 | 17 | d | 11-17d | SWH Heater Fuel Type in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is true | Yes | Per SHW Heater | Fuel Type of the SHW Heater in the Baseline RMR does not equal the expected value | Baseline | Fail | The fuel type of the SHW Heater <service_water_heating heater_name> in the Baseline RMR is not correct | service_water_heating:heater_name service_water_heating:heater_fuel_type service_water_heating:building_area_type |  |  | SWH_Heater1 electric Dormitory | One Story Template
11 | 18 | a | 11-18a | SWH Heater Efficiency in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is True | Yes | Per SHW Heater | Efficiency of the SHW Heater in the Baseline RMR equals the expected value | Baseline | Pass | The efficiency of SHW Heater <service_water_heating heater_name> in the Baseline RMR is correct | service_water_heating:heater_name service_water_heating:heater_efficiency |  |  |  |  | Can't be determined
11 | 18 | b | 11-18b | SWH Heater Efficiency in Baseline RMR = expected value | Baseline RMR = expected value | Rule 11-4 is True | Yes | Per SHW Heater | Efficiency of the SHW Heater in the Baseline RMR does not equal the expected value | Baseline | Fail | The efficiency of SHW Heater <service_water_heating heater_name> in the Baseline RMR is not correct | service_water_heating:heater_name service_water_heating:heater_efficiency |  |  |  |  | Can't be determined
11 | 19 | a | 11-19a | Baseline RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Baseline RMR = User RMR | none | No | Per Project | service_water_heating energy in Baseline RMR = User RMR | Baseline | Pass | Annual service_water_heating energy is the same in both the Baseline and User RMR files | service_water_heating:annual_enduse_electricity service_water_heating:annual_enduse_fossilfuel | 10000 0 |  | 10000 0
11 | 19 | b | 11-19b | Baseline RMR SWH annual energy enduse equals User RMR SWH annual energy end use | Baseline RMR = User RMR | none | No | Per Project | service_water_heating energy in Baseline RMR does not equal User RMR | Baseline | Fail | Annual service_water_heating energy is not the same in the Baseline and User RMR files | service_water_heating:annual_enduse_electricity service_water_heating:annual_enduse_fossilfuel | 10000 0 |  | 15000 0
Note on S27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)
Note on S45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Write clear statement, is this correct? (Y/N)