ASHRAE STD 229P RULESET CHECKING TOOL

Project Testing Report

Ruleset: ASHRAE 90.1-2019 Performance Rating Method (Appendix G)

Date: 09-03-2021

# RMR Files

**User:** user\_rmr.json

**Baseline:** baseline\_rmr.json

**Proposed:** proposed\_rmr.json

# Summary

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **All Sections** | **Lighting** | **Receptacles** | **Transformers** |
| **Rules** | 11 | 2 | 3 | 6 |
| **Rule Evaluations** | 21 | 5 | 6 | 10 |
| **Passed** | 19 | 5 | 6 | 8 |
| **Failed** | 1 | 0 | 0 | 1 |
| **Missing Context** | 0 | 0 | 0 | 0 |
| **Not Applicable** | 1 | 0 | 0 | 1 |
| **Manual Check Required** | 0 | 0 | 0 | 0 |

### Failing Rules

* 15-6

# Detailed

**Id:** 6-1

**Description:** For the proposed building, each space has the same lighting power as the corresponding space in the U-RMR

**RMR Context:** /buildings

### Evaluations

**RMR Context:** /spaces

**Id:** 1

**Name:** Space 1

**Outcome:** PASSED

**Calculated Values:**

* + space\_lighting\_power\_user: 41.0
  + space\_lighting\_power\_proposed: 41.0

**RMR Context:** /spaces

**Id:** 2

**Name:** Space2

**Outcome:** PASSED

**Calculated Values:**

* + space\_lighting\_power\_user: 110.0
  + space\_lighting\_power\_proposed: 110.0